Failure Frequency due to Natural Landsliding

TD/2 Ed 2 & PD 8010-3:2013

Landsliding model predictions assuming 60% poor quality and 40% good quality girth welds for average wall thickness (10mm)

Ruptures = (0.6 x 0.0248 + 0.4 x 0.0075)0.02

= 3.576x10-4 per1000kmyrs

Leaks = 0.223 x 0.02 = 4.4626x10-3 per 1000kmyrs

National Grid updated (weighted average) predictions:

Ruptures = 1.6 x 10-4 per 1000 kmyrs

Leaks = 4.4x10-4 per 1000 kmyrs

Comparison with operational data:

| Prediction | Failure Frequency (1000 kmyrs) |  |
| --- | --- | --- |
|  | Ruptures | Leaks |
| UKOPA | 1.0x10-3 | 6.0x10-3 |
| EGIG | 1.08x10-2 | 1.53x10-2 |
| TD/2&PD 8010-3 | 3.58x10-4 | 4.46x10-3 |
| National Grid Updated | 1.6x10-4 | 4.4x10-4 |