## INTRODUCTION
Example Drain Down Calculator
dated march 2016
These spreadsheets provide the data to estimate the quantity and drain down duration which could occur from a leak in a pipeline.
Drain Down Quantity shows the amount of drain down at any point along the pipeline route, starting at point A.
The only input data required is the Distance from Point A in kilometres, which may come from the leak detection system.
The data shown is the amount of drain down with the Block Valves left open, and with the Block Valves closed (assuming they are closed
immediately after the pumps are switched off). 20m3 is included for 5 minutes to switch off pumps, and 10m3 is included for liquid
expansion. The sheet display also recommends which block valves should be closed.
Drain Down Times shows how long (in hours) the vacuum drain down quantity will take to drain out after the block valves
are closed. The times are automatically displayed once the distance has been entered in the previous sheet. No extra data is required.
Times are shown for 4 cases - pipeline rupure, a large hole (2 inch diameter), medium hole (1 inch) and small hole (half inch).
Chainage and Names to help locate the leak chainage based on place name or road/rail/river crossing - by chainage or alphabetical
Drain Down Graph shows the drain down amount at each point along the length of the pipeline. The red line shows the amount
with the Block Valves open and the green line shows the drain down with the Block Valves closed. The height profile of the pipeline is
also shown as a black line, and the location of the Block Valves is shown as blue squares. No input data is required for Sheet 3.
Profile and Data shows the height profile for the pipeline derived from the original As Built Plan and Profile drawings,
along with other data used for the calculation of drain down, pipeline length and diameter, product density, and location of Block Valves.
NOTE - Calculations are carried out in a separate workbook - this is an example of the control room data workbook only.
Contact rodmcconnell@btinternet.com for further details

## Drain Down Quantity
Typical Pipeline - Drain Down Quantity
DIRECTION - from Point A to Point Z
| INPUT DATA >> Leak Distance from Point A | 34 | km
| Total Drain-Down with Valves Open | 213.3882 | m3
| Drain-Down with Block Valves Closed | 47.3882 | m3
| Recommend closing Upstream Block Valve at | Valve 4 at 30km
| because it could reduce drain down by up to | 166 | m3
Distance from Point A - km | Total Drain Down with Block Valves Open m3 | Drain Down with Block Valves Immediately Closed m3 | Upstream Block Valve recommended | Upstream Block Valve - reduction in drain down m3 | Downstream Block Valve recommended | Downstream BV reduction in drain down m3 | Rupture - Time to Drain - Hours | 50 mm Hole - Time to Drain | 25 mm Hole - Time to Drain | 12.5 mm Hole - Time to Drain
0 | 535.6751 | 91.5751 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.2 | 4.9 | 19.5
0.1 | 540.9751 | 96.8751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.4 | 5.5 | 21.9
0.2 | 544.9878 | 100.8878 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.2 | 4.9 | 19.5
0.3 | 555.738 | 111.638 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.5 | 5.8 | 23.2
0.4 | 566.3882 | 122.2882 |  |  | Valve 1 at 10km | 444.1 | 1 | 1.9 | 7.4 | 29.8
0.5 | 561.038 | 116.938 |  |  | Valve 1 at 10km | 444.1 | 1 | 1.8 | 7.2 | 29
0.6 | 550.3878 | 106.2878 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.4 | 5.4 | 21.8
0.7 | 546.3751 | 102.2751 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.4 | 5.6 | 22.4
0.8 | 555.738 | 111.638 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.4 | 5.6 | 22.3
0.9 | 544.9878 | 100.8878 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.3 | 5.1 | 20.5
1 | 540.9751 | 96.8751 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.4 | 5.4 | 21.7
1.1 | 550.3878 | 106.2878 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.6 | 6.3 | 25
1.2 | 546.3751 | 102.2751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.6 | 6.3 | 25.1
1.3 | 546.3751 | 102.2751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.6 | 6.3 | 25.2
1.4 | 554.4004 | 110.3004 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.5 | 5.8 | 23.2
1.5 | 540.9751 | 96.8751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.5 | 6.1 | 24.5
1.6 | 550.3878 | 106.2878 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.4 | 5.5 | 21.8
1.7 | 577.138 | 133.038 |  |  | Valve 1 at 10km | 444.1 | 0.9 | 2.1 | 8.5 | 33.8
1.8 | 567.7751 | 123.6751 |  |  | Valve 1 at 10km | 444.1 | 0.9 | 2.1 | 8.4 | 33.7
1.9 | 571.7878 | 127.6878 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.9 | 7.5 | 30.1
2 | 571.7878 | 127.6878 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.9 | 7.5 | 29.9
2.1 | 567.7751 | 123.6751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.9 | 7.7 | 31
2.2 | 581.2004 | 137.0004 |  |  | Valve 1 at 10km | 444.2 | 0.9 | 2.2 | 9 | 35.9
2.3 | 567.7751 | 123.6751 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.8 | 7.2 | 28.6
2.4 | 577.138 | 133.038 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.8 | 7.2 | 28.8
2.5 | 571.7878 | 127.6878 |  |  | Valve 1 at 10km | 444.1 | 1 | 2.4 | 9.7 | 39
2.6 | 557.0751 | 112.9751 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 2 | 8.2 | 32.7
2.7 | 571.7878 | 127.6878 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 2.2 | 8.6 | 34.5
2.8 | 613.2519 | 169.1519 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.9 | 7.6 | 30.2
2.9 | 598.5388 | 154.4388 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 2.1 | 8.4 | 33.8
3 | 582.4886 | 138.3886 |  |  | Valve 1 at 10km | 444.1 | 0.8 | 1.9 | 7.8 | 31
3.1 | 571.7384 | 127.6384 |  |  | Valve 1 at 10km | 444.1 | 0.6 | 1.5 | 6.1 | 24.5
3.2 | 566.3882 | 122.2882 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.8 | 7.1 | 28.4
3.3 | 555.738 | 111.638 |  |  | Valve 1 at 10km | 444.1 | 0.7 | 1.6 | 6.3 | 25.3
3.4 | 544.9878 | 100.8878 |  |  | Valve 1 at 10km | 444.1 | 0.6 | 1.4 | 5.4 | 21.8
3.5 | 535.6751 | 91.5751 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.3 | 5 | 20
3.6 | 549.0506 | 104.9506 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.2 | 4.8 | 19.1
3.7 | 539.6878 | 95.5878 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.3 | 5.3 | 21.4
3.8 | 535.6751 | 91.5751 |  |  | Valve 1 at 10km | 444.1 | 0.6 | 1.4 | 5.6 | 22.4
3.9 | 539.6878 | 95.5878 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.4 | 5.5 | 22
4 | 535.6751 | 91.5751 |  |  | Valve 1 at 10km | 444.1 | 0.6 | 1.7 | 6.8 | 27
4.1 | 539.6878 | 95.5878 |  |  | Valve 1 at 10km | 444.1 | 0.6 | 1.5 | 6.2 | 24.7
4.2 | 575.7515 | 131.6515 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 4.9 | 19.6
4.3 | 555.7384 | 111.6384 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 4.8 | 19.2
4.4 | 550.3882 | 106.2882 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.3 | 5.1 | 20.3
4.5 | 545.038 | 100.938 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.3 | 5.3 | 21.4
4.6 | 539.6878 | 95.5878 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.4 | 5.8 | 23
4.7 | 530.2751 | 86.1751 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.3 | 5.4 | 21.5
4.8 | 539.638 | 95.538 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.4 | 5.5 | 21.9
4.9 | 528.9878 | 84.8878 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 4.6 | 18.5
5 | 519.5751 | 75.4751 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 4.7 | 18.6
5.1 | 533.0004 | 88.9004 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.1 | 4.5 | 17.9
5.2 | 514.2751 | 70.1751 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 4.9 | 19.7
5.3 | 523.638 | 79.538 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.2 | 5 | 19.8
5.4 | 518.2878 | 74.1878 |  |  | Valve 1 at 10km | 444.1 | 0.5 | 1.4 | 5.5 | 22.1
5.5 | 498.1751 | 54.0751 |  |  | Valve 1 at 10km | 444.1 | 0.2 | 0.6 | 2.5 | 9.9
5.6 | 523.5878 | 79.4878 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.2 | 4.6 | 18.4
5.7 | 534.338 | 90.238 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.4 | 5.7 | 22.8
5.8 | 549.0511 | 104.9511 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.2 | 4.8 | 19.2
5.9 | 523.5878 | 79.4878 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.1 | 4.6 | 18.3
6 | 519.5751 | 75.4751 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.2 | 4.7 | 18.7
6.1 | 528.9878 | 84.8878 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.6 | 6.4 | 25.7
6.2 | 539.638 | 95.538 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.5 | 6 | 23.9
6.3 | 581.1021 | 137.0021 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.3 | 5.1 | 20.4
6.4 | 561.0388 | 116.9388 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.3 | 5.3 | 21.2
6.5 | 555.6886 | 111.5886 |  |  | Valve 1 at 10km | 444.1 | 0.4 | 1.6 | 6.3 | 25
6.6 | 550.3886 | 106.2886 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.2 | 4.7 | 19
6.7 | 545.0388 | 100.9388 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.3 | 5 | 20.2
6.8 | 539.6392 | 95.5392 |  |  | Valve 1 at 10km | 444.1 | 0.2 | 0.8 | 3.1 | 12.6
6.9 | 528.9392 | 84.8392 |  |  | Valve 1 at 10km | 444.1 | 0.2 | 0.5 | 2.1 | 8.6
7 | 507.589 | 68.789 |  |  | Valve 1 at 10km | 438.8 | 0 | 0 | 0 | 0
7.1 | 496.8388 | 63.4388 |  |  | Valve 1 at 10km | 433.4 | 0 | 0 | 0 | 0
7.2 | 486.1886 | 58.0886 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
7.3 | 480.8384 | 52.7384 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
7.4 | 464.7882 | 47.3882 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
7.5 | 459.438 | 42.038 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
7.6 | 454.0878 | 36.6878 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
7.7 | 444.6751 | 32.6751 |  |  | Valve 1 at 10km | 412 | 0 | 0 | 0 | 0
7.8 | 448.6878 | 36.6878 |  |  | Valve 1 at 10km | 412 | 0 | 0 | 0 | 0
7.9 | 459.438 | 42.038 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
8 | 464.7882 | 47.3882 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
8.1 | 480.8384 | 52.7384 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
8.2 | 491.4886 | 58.0886 |  |  | Valve 1 at 10km | 433.4 | 0 | 0 | 0 | 0
8.3 | 518.2388 | 74.1388 |  |  | Valve 1 at 10km | 444.1 | 0.1 | 0.5 | 2 | 8
8.4 | 549.0523 | 104.9523 |  |  | Valve 1 at 10km | 444.1 | 0.1 | 0.8 | 3.2 | 12.8
8.5 | 496.8882 | 52.7882 |  |  | Valve 1 at 10km | 444.1 | 0.3 | 1.1 | 4.6 | 18.3
8.6 | 470.138 | 42.038 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
8.7 | 464.7878 | 36.6878 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
8.8 | 450.0751 | 32.6751 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
8.9 | 468.8008 | 51.4008 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
9 | 459.438 | 42.038 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
9.1 | 437.9878 | 36.6878 |  |  | Valve 1 at 10km | 401.3 | 0 | 0 | 0 | 0
9.2 | 428.6751 | 32.6751 |  |  | Valve 1 at 10km | 396 | 0 | 0 | 0 | 0
9.3 | 437.9878 | 36.6878 |  |  | Valve 1 at 10km | 401.3 | 0 | 0 | 0 | 0
9.4 | 454.038 | 42.038 |  |  | Valve 1 at 10km | 412 | 0 | 0 | 0 | 0
9.5 | 479.4511 | 56.7511 |  |  | Valve 1 at 10km | 422.7 | 0 | 0 | 0 | 0
9.6 | 454.0878 | 36.6878 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
9.7 | 428.6751 | 32.6751 |  |  | Valve 1 at 10km | 396 | 0 | 0 | 0 | 0
9.8 | 437.9878 | 36.6878 |  |  | Valve 1 at 10km | 401.3 | 0 | 0 | 0 | 0
9.9 | 459.438 | 42.038 |  |  | Valve 1 at 10km | 417.4 | 0 | 0 | 0 | 0
10 | 495.5515 | 67.4515 |  |  | Valve 1 at 10km | 428.1 | 0 | 0 | 0 | 0
10.1 | 464.7882 | 245.3882 |  |  | Valve 2 at 15km | 219.4 | 0.8 | 2.1 | 8.2 | 32.8
10.2 | 454.038 | 234.738 |  |  | Valve 2 at 15km | 219.3 | 0.9 | 2.2 | 9 | 35.9
10.3 | 432.6878 | 213.2878 |  |  | Valve 2 at 15km | 219.4 | 0.7 | 1.7 | 6.7 | 26.7
10.4 | 428.6751 | 209.2751 |  |  | Valve 2 at 15km | 219.4 | 0.7 | 1.7 | 6.8 | 27.2
10.5 | 484.8013 | 265.5013 |  |  | Valve 2 at 15km | 219.3 | 0.8 | 2.5 | 10.1 | 40.6
10.6 | 475.4886 | 256.0886 |  |  | Valve 2 at 15km | 219.4 | 0.8 | 2.3 | 9.1 | 36.4
10.7 | 454.0384 | 234.7384 |  |  | Valve 2 at 15km | 219.3 | 0.8 | 1.9 | 7.8 | 31.1
10.8 | 443.3882 | 223.9882 |  |  | Valve 2 at 15km | 219.4 | 0.6 | 1.7 | 7 | 27.8
10.9 | 432.638 | 213.338 |  |  | Valve 2 at 15km | 219.3 | 0.6 | 1.6 | 6.5 | 26.2
11 | 427.2878 | 207.9878 |  |  | Valve 2 at 15km | 219.3 | 0.7 | 1.8 | 7.2 | 28.8
11.1 | 423.2751 | 203.9751 |  |  | Valve 2 at 15km | 219.3 | 0.7 | 1.8 | 7.4 | 29.5
11.2 | 427.2878 | 207.9878 |  |  | Valve 2 at 15km | 219.3 | 0.6 | 1.6 | 6.5 | 26.1
11.3 | 442.0506 | 222.6506 |  |  | Valve 2 at 15km | 219.4 | 0.7 | 1.9 | 7.5 | 30.1
11.4 | 423.2751 | 203.9751 |  |  | Valve 2 at 15km | 219.3 | 0.5 | 1.7 | 6.7 | 26.6
11.5 | 442.0008 | 222.7008 |  |  | Valve 2 at 15km | 219.3 | 0.5 | 1.7 | 6.6 | 26.5
11.6 | 432.638 | 213.338 |  |  | Valve 2 at 15km | 219.3 | 0.6 | 1.8 | 7.1 | 28.2
11.7 | 421.9878 | 202.5878 |  |  | Valve 2 at 15km | 219.4 | 0.6 | 1.7 | 6.9 | 27.6
11.8 | 417.9751 | 198.5751 |  |  | Valve 2 at 15km | 219.4 | 0.6 | 1.9 | 7.4 | 29.8
11.9 | 417.9751 | 198.5751 |  |  | Valve 2 at 15km | 219.4 | 0.6 | 1.8 | 7.4 | 29.6
12 | 421.9878 | 202.5878 |  |  | Valve 2 at 15km | 219.4 | 0.5 | 1.8 | 7.1 | 28.2
12.1 | 438.0384 | 218.6384 |  |  | Valve 2 at 15km | 219.4 | 0.5 | 1.8 | 7 | 28.2
12.2 | 432.6882 | 213.2882 |  |  | Valve 2 at 15km | 219.4 | 0.6 | 1.9 | 7.5 | 30
12.3 | 427.2882 | 207.9882 |  |  | Valve 2 at 15km | 219.3 | 0.4 | 1.7 | 6.7 | 26.9
12.4 | 421.9882 | 202.5882 |  |  | Valve 2 at 15km | 219.4 | 0.5 | 1.7 | 7 | 27.8
12.5 | 416.5886 | 197.2886 |  |  | Valve 2 at 15km | 219.3 | 0.4 | 1.6 | 6.3 | 25.1
12.6 | 411.2388 | 191.8388 |  |  | Valve 2 at 15km | 219.4 | 0.4 | 1.4 | 5.6 | 22.4
12.7 | 405.8886 | 186.4886 |  |  | Valve 2 at 15km | 219.4 | 0.5 | 1.7 | 6.7 | 26.7
12.8 | 400.5886 | 181.1886 |  |  | Valve 2 at 15km | 219.4 | 0.4 | 1.5 | 6 | 24.1
12.9 | 395.1886 | 175.7886 |  |  | Valve 2 at 15km | 219.4 | 0.4 | 1.4 | 5.7 | 22.6
13 | 389.8384 | 170.4384 |  |  | Valve 2 at 15km | 219.4 | 0.5 | 1.6 | 6.5 | 26.2
13.1 | 384.4886 | 165.0886 |  |  | Valve 2 at 15km | 219.4 | 0.4 | 1.5 | 6.2 | 24.8
13.2 | 379.1388 | 159.7388 |  |  | Valve 2 at 15km | 219.4 | 0.3 | 1.2 | 4.7 | 18.7
13.3 | 373.8388 | 154.4388 |  |  | Valve 2 at 15km | 219.4 | 0.3 | 1.2 | 4.9 | 19.4
13.4 | 368.4388 | 149.0388 |  |  | Valve 2 at 15km | 219.4 | 0.3 | 1.2 | 4.8 | 19.2
13.5 | 363.0388 | 143.7388 |  |  | Valve 2 at 15km | 219.3 | 0.3 | 1.1 | 4.4 | 17.8
13.6 | 357.6886 | 138.3886 |  |  | Valve 2 at 15km | 219.3 | 0.3 | 1.2 | 4.8 | 19.1
13.7 | 352.3384 | 133.0384 |  |  | Valve 2 at 15km | 219.3 | 0.3 | 1.3 | 5.2 | 21
13.8 | 347.0384 | 127.6384 |  |  | Valve 2 at 15km | 219.4 | 0.2 | 1.1 | 4.3 | 17.2
13.9 | 341.6384 | 122.3384 |  |  | Valve 2 at 15km | 219.3 | 0.2 | 1 | 4 | 16.1
14 | 336.3384 | 116.9384 |  |  | Valve 2 at 15km | 219.4 | 0.2 | 0.9 | 3.6 | 14.4
14.1 | 330.9882 | 111.5882 |  |  | Valve 2 at 15km | 219.4 | 0.3 | 1.2 | 4.8 | 19.3
14.2 | 325.5882 | 106.2882 |  |  | Valve 2 at 15km | 219.3 | 0.2 | 1 | 4 | 16.1
14.3 | 320.2882 | 100.8882 |  |  | Valve 2 at 15km | 219.4 | 0.2 | 0.9 | 3.5 | 13.9
14.4 | 314.8882 | 95.5882 |  |  | Valve 2 at 15km | 219.3 | 0.1 | 0.8 | 3.2 | 12.7
14.5 | 309.538 | 90.238 |  |  | Valve 2 at 15km | 219.3 | 0.2 | 1.1 | 4.5 | 18
14.6 | 304.1882 | 84.8882 |  |  | Valve 2 at 15km | 219.3 | 0.1 | 0.7 | 2.9 | 11.6
14.7 | 298.8882 | 47.3882 |  |  | Valve 2 at 15km | 251.5 | 0 | 0 | 0 | 0
14.8 | 293.4882 | 47.3882 |  |  | Valve 2 at 15km | 246.1 | 0 | 0 | 0 | 0
14.9 | 282.8388 | 63.4388 |  |  | Valve 2 at 15km | 219.4 | 0 | 0 | 0 | 0
15 | 250.6886 | 58.0886 |  |  | Valve 2 at 15km | 192.6 | 0 | 0 | 0 | 0
15.1 | 213.2384 | 213.2384 |  |  |  |  | 2.2 | 4.2 | 17 | 68
15.2 | 186.4882 | 186.4882 |  |  |  |  | 1.9 | 3.7 | 15 | 59.9
15.3 | 159.738 | 159.738 |  |  |  |  | 1.7 | 3.3 | 13.3 | 53.3
15.4 | 143.6878 | 143.6878 |  |  |  |  | 1.5 | 2.9 | 11.5 | 45.9
15.5 | 134.3751 | 134.3751 |  |  |  |  | 1.7 | 3.5 | 13.8 | 55.3
15.6 | 128.9751 | 128.9751 |  |  |  |  | 1.6 | 3.2 | 12.8 | 51.1
15.7 | 179.8008 | 179.8008 |  |  |  |  | 2 | 4.3 | 17.1 | 68.3
15.8 | 159.738 | 159.738 |  |  |  |  | 1.7 | 3.4 | 13.5 | 53.9
15.9 | 149.0878 | 149.0878 |  |  |  |  | 1.8 | 3.6 | 14.6 | 58.3
16 | 139.6751 | 139.6751 |  |  |  |  | 1.6 | 3.1 | 12.6 | 50.2
16.1 | 139.6751 | 139.6751 |  |  |  |  | 1.5 | 3.1 | 12.3 | 49.2
16.2 | 143.6878 | 143.6878 |  |  |  |  | 1.5 | 3.1 | 12.4 | 49.6
16.3 | 134.3751 | 134.3751 |  |  |  |  | 1.6 | 3.5 | 13.8 | 55.3
16.4 | 143.6878 | 143.6878 |  |  |  |  | 1.5 | 3.2 | 13 | 51.8
16.5 | 159.738 | 159.738 |  |  |  |  | 1.5 | 3.2 | 12.7 | 50.6
16.6 | 190.5008 | 190.5008 |  |  |  |  | 1.7 | 3.9 | 15.4 | 61.6
16.7 | 166.4751 | 166.4751 |  |  |  |  | 1.6 | 3.7 | 14.7 | 58.7
16.8 | 175.7878 | 175.7878 |  |  |  |  | 1.6 | 3.7 | 14.8 | 59.1
16.9 | 186.538 | 186.538 |  |  |  |  | 1.6 | 3.7 | 15 | 59.9
17 | 202.5882 | 202.5882 |  |  |  |  | 1.8 | 4.3 | 17.1 | 68.3
17.1 | 207.9384 | 207.9384 |  |  |  |  | 1.9 | 4.4 | 17.7 | 70.9
17.2 | 191.8882 | 191.8882 |  |  |  |  | 1.6 | 3.8 | 15.1 | 60.2
17.3 | 159.738 | 159.738 |  |  |  |  | 1.4 | 3.4 | 13.6 | 54.4
17.4 | 122.2878 | 122.2878 |  |  |  |  | 1.2 | 2.8 | 11.2 | 44.9
17.5 | 107.5751 | 107.5751 |  |  |  |  | 1.1 | 2.6 | 10.3 | 41.1
17.6 | 115.6004 | 115.6004 |  |  |  |  | 1 | 2.2 | 9 | 35.9
17.7 | 96.8751 | 96.8751 |  |  |  |  | 0.9 | 2.1 | 8.5 | 34.1
17.8 | 100.8878 | 100.8878 |  |  |  |  | 1 | 2.2 | 8.9 | 35.6
17.9 | 86.1751 | 86.1751 |  |  |  |  | 0.8 | 1.7 | 6.7 | 27
18 | 106.2878 | 106.2878 |  |  |  |  | 1 | 2.5 | 9.9 | 39.6
18.1 | 116.938 | 116.938 |  |  |  |  | 0.9 | 2.1 | 8.5 | 33.9
18.2 | 127.6882 | 127.6882 |  |  |  |  | 0.9 | 2.4 | 9.6 | 38.3
18.3 | 137.0511 | 137.0511 |  |  |  |  | 0.9 | 2.2 | 8.8 | 35.3
18.4 | 112.9751 | 112.9751 |  |  |  |  | 1 | 2.5 | 9.9 | 39.7
18.5 | 147.7013 | 147.7013 |  |  |  |  | 1 | 2.5 | 10.2 | 40.6
18.6 | 127.6384 | 127.6384 |  |  |  |  | 0.8 | 2.1 | 8.2 | 33
18.7 | 122.2882 | 122.2882 |  |  |  |  | 0.9 | 2.4 | 9.7 | 38.7
18.8 | 111.638 | 111.638 |  |  |  |  | 0.9 | 2.4 | 9.7 | 39
18.9 | 90.1878 | 90.1878 |  |  |  |  | 0.7 | 1.7 | 6.7 | 26.8
19 | 80.8751 | 80.8751 |  |  |  |  | 0.5 | 1.2 | 5 | 19.8
19.1 | 138.3899 | 138.3899 |  |  |  |  | 0.5 | 1.3 | 5 | 20.2
19.2 | 133.0397 | 133.0397 |  |  |  |  | 0.5 | 1.3 | 5.2 | 20.9
19.3 | 127.6895 | 127.6895 |  |  |  |  | 0.6 | 1.5 | 5.9 | 23.4
19.4 | 116.9392 | 116.9392 |  |  |  |  | 0.5 | 1.2 | 4.8 | 19.4
19.5 | 111.589 | 111.589 |  |  |  |  | 0.5 | 1.4 | 5.5 | 21.9
19.6 | 106.2388 | 106.2388 |  |  |  |  | 0.7 | 1.7 | 6.8 | 27.2
19.7 | 95.5886 | 95.5886 |  |  |  |  | 0.7 | 1.7 | 6.7 | 26.8
19.8 | 90.2384 | 90.2384 |  |  |  |  | 0.9 | 2.3 | 9 | 36.2
19.9 | 74.1882 | 74.1882 |  |  |  |  | 0.6 | 1.3 | 5.3 | 21
20 | 68.838 | 68.838 |  |  |  |  | 0.9 | 2 | 7.9 | 31.7
20.1 | 52.7878 | 52.7878 |  |  |  |  | 0.5 | 1 | 4.1 | 16.6
20.2 | 43.3751 | 43.3751 |  |  |  |  | 0.5 | 1 | 4.2 | 16.7
20.3 | 58.0882 | 58.0882 |  |  |  |  | 0.6 | 1.3 | 5.3 | 21.4
20.4 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
20.5 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
20.6 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
20.7 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
20.8 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
20.9 | 58.0886 | 58.0886 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21 | 52.7384 | 52.7384 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.1 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.2 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.3 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.4 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.5 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.6 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.7 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.8 | 62.1013 | 62.1013 |  |  |  |  | 0 | 0.1 | 0.5 | 1
21.9 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.1 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.2 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.3 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.4 | 56.7511 | 56.7511 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.5 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.6 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.7 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.8 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
22.9 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23 | 46.0506 | 46.0506 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.1 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.2 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.3 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.4 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.5 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.6 | 52.7384 | 52.7384 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.7 | 99.5527 | 99.5527 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.8 | 68.789 | 68.789 |  |  |  |  | 0 | 0.1 | 0.5 | 1
23.9 | 63.4388 | 63.4388 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24 | 58.0886 | 58.0886 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.1 | 52.7384 | 52.7384 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.2 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.3 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.4 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.5 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.6 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.7 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.8 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
24.9 | 52.7384 | 52.7384 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25 | 58.0886 | 58.0886 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.1 | 67.4515 | 67.4515 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.2 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.3 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.4 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.5 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.6 | 62.1013 | 62.1013 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.7 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.8 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
25.9 | 32.6751 | 32.6751 |  |  |  |  | 0 | 0.1 | 0.5 | 1
26 | 36.6878 | 36.6878 |  |  |  |  | 0 | 0.1 | 0.5 | 1
26.1 | 42.038 | 42.038 |  |  |  |  | 0 | 0.1 | 0.5 | 1
26.2 | 47.3882 | 47.3882 |  |  |  |  | 0 | 0.1 | 0.5 | 1
26.3 | 68.8384 | 52.7384 |  |  |  |  | 0 | 0.1 | 0.5 | 1
26.4 | 95.5886 | 58.0886 | Valve 3 at 26km | 37.5 |  |  | 0 | 0.1 | 0.5 | 1
26.5 | 111.6384 | 68.8384 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 3.9 | 15.7
26.6 | 116.9886 | 74.1886 | Valve 3 at 26km | 42.8 |  |  | 0.1 | 0.5 | 1.9 | 7.6
26.7 | 122.2886 | 79.4886 | Valve 3 at 26km | 42.8 |  |  | 0.1 | 0.7 | 2.8 | 11.1
26.8 | 127.6388 | 84.8388 | Valve 3 at 26km | 42.8 |  |  | 0.1 | 0.5 | 2.1 | 8.2
26.9 | 132.9886 | 90.1886 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 0.9 | 3.6 | 14.4
27 | 138.3384 | 95.5384 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 0.9 | 3.7 | 14.9
27.1 | 143.7384 | 100.9384 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 0.9 | 3.7 | 15
27.2 | 149.0882 | 106.2882 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1.1 | 4.2 | 17
27.3 | 154.3882 | 111.5882 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 4 | 16.1
27.4 | 159.7882 | 116.9882 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1.2 | 4.9 | 19.7
27.5 | 165.0882 | 122.2882 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1.1 | 4.2 | 16.9
27.6 | 170.4878 | 127.6878 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.5 | 6 | 23.9
27.7 | 175.7878 | 132.9878 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 4.1 | 16.2
27.8 | 181.1878 | 138.3878 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1.2 | 4.6 | 18.5
27.9 | 186.5878 | 143.7878 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1.2 | 4.6 | 18.5
28 | 193.2751 | 150.4751 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1.3 | 5.4 | 21.4
28.1 | 197.2878 | 154.4878 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 4.1 | 16.5
28.2 | 217.3511 | 174.5511 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 3.9 | 15.6
28.3 | 202.638 | 159.838 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 3.9 | 15.8
28.4 | 197.2878 | 154.4878 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 4 | 16.1
28.5 | 193.2751 | 150.4751 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1 | 4.2 | 16.8
28.6 | 197.2878 | 154.4878 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1 | 4.1 | 16.2
28.7 | 202.638 | 159.838 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 1 | 3.8 | 15.2
28.8 | 207.9882 | 165.1882 | Valve 3 at 26km | 42.8 |  |  | 0.2 | 0.9 | 3.8 | 15
28.9 | 218.7384 | 175.9384 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1.2 | 4.7 | 18.7
29 | 224.0886 | 181.2886 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1.1 | 4.4 | 17.4
29.1 | 229.3886 | 186.5886 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.5 | 6.2 | 24.7
29.2 | 234.7886 | 191.9886 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.6 | 6.3 | 25.1
29.3 | 240.1388 | 197.3388 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.4 | 5.5 | 21.9
29.4 | 245.489 | 202.689 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.3 | 5.2 | 20.9
29.5 | 276.2527 | 233.4527 | Valve 3 at 26km | 42.8 |  |  | 0.3 | 1.2 | 4.9 | 19.7
29.6 | 229.4384 | 186.6384 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.2 | 5 | 20
29.7 | 224.0882 | 181.2882 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.3 | 5.2 | 20.7
29.8 | 213.338 | 170.538 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.3 | 5.1 | 20.3
29.9 | 207.9878 | 165.1878 | Valve 3 at 26km | 42.8 |  |  | 0.4 | 1.3 | 5.2 | 20.7
30 | 198.6751 | 32.6751 | Valve 3 at 26km | 166 |  |  | 0 | 0.1 | 0.5 | 1
30.1 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
30.2 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
30.3 | 213.338 | 42.038 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
30.4 | 233.4013 | 62.1013 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
30.5 | 213.338 | 42.038 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
30.6 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
30.7 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
30.8 | 222.7506 | 46.0506 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
30.9 | 213.3878 | 36.6878 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
31 | 209.3751 | 32.6751 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
31.1 | 233.4511 | 56.7511 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
31.2 | 224.0882 | 47.3882 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
31.3 | 213.338 | 42.038 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
31.4 | 207.9878 | 36.6878 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
31.5 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
31.6 | 208.038 | 42.038 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
31.7 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
31.8 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
31.9 | 206.7004 | 40.7004 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.1 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.2 | 222.7511 | 56.7511 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.3 | 208.038 | 42.038 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.4 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.5 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.6 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.7 | 212.0506 | 46.0506 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.8 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
32.9 | 212.0506 | 46.0506 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.1 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.2 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.3 | 208.038 | 42.038 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.4 | 213.3882 | 47.3882 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.5 | 228.1013 | 62.1013 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.6 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.7 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.8 | 202.6878 | 36.6878 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
33.9 | 208.038 | 42.038 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
34 | 213.3882 | 47.3882 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
34.1 | 198.6751 | 32.6751 | Valve 4 at 30km | 166 |  |  | 0 | 0.1 | 0.5 | 1
34.2 | 207.9878 | 36.6878 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
34.3 | 218.738 | 42.038 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
34.4 | 224.0882 | 47.3882 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
34.5 | 240.1384 | 52.7384 | Valve 4 at 30km | 187.4 |  |  | 0 | 0.1 | 0.5 | 1
34.6 | 270.9013 | 83.5013 | Valve 4 at 30km | 187.4 |  |  | 0.5 | 2 | 7.9 | 31.5
34.7 | 225.3751 | 38.0751 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 0.9 | 3.8 | 15
34.8 | 265.5013 | 78.2013 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.7 | 6.8 | 27.1
34.9 | 234.7384 | 52.7384 | Valve 4 at 30km | 182 |  |  | 0 | 0.1 | 0.5 | 1
35 | 224.0882 | 47.3882 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
35.1 | 218.738 | 42.038 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
35.2 | 213.3878 | 36.6878 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
35.3 | 203.9751 | 32.6751 | Valve 4 at 30km | 171.3 |  |  | 0 | 0.1 | 0.5 | 1
35.4 | 213.3878 | 36.6878 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
35.5 | 218.738 | 42.038 | Valve 4 at 30km | 176.7 |  |  | 0 | 0.1 | 0.5 | 1
35.6 | 240.0882 | 52.7882 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 0.7 | 2.8 | 11.3
35.7 | 276.2013 | 88.9013 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 0.9 | 3.7 | 15
35.8 | 250.7878 | 63.4878 | Valve 4 at 30km | 187.3 |  |  | 0.4 | 1.2 | 4.8 | 19.1
35.9 | 230.7751 | 43.3751 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 0.9 | 3.6 | 14.5
36 | 245.4878 | 58.0878 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 1 | 4.1 | 16.6
36.1 | 256.138 | 68.838 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 1 | 4 | 16.2
36.2 | 292.3013 | 104.9013 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 1.4 | 5.5 | 22
36.3 | 261.538 | 74.138 | Valve 4 at 30km | 187.4 |  |  | 0.3 | 1 | 4 | 15.9
36.4 | 250.7878 | 63.4878 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 0.9 | 3.5 | 14.1
36.5 | 246.7751 | 59.4751 | Valve 4 at 30km | 187.3 |  |  | 0.4 | 1 | 4.1 | 16.6
36.6 | 250.7878 | 63.4878 | Valve 4 at 30km | 187.3 |  |  | 0.4 | 1 | 3.8 | 15.3
36.7 | 270.9008 | 83.5008 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 1.1 | 4.3 | 17.2
36.8 | 250.7878 | 63.4878 | Valve 4 at 30km | 187.3 |  |  | 0.3 | 0.9 | 3.7 | 14.6
36.9 | 246.7751 | 59.4751 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.5 | 6.1 | 24.5
37 | 250.7878 | 63.4878 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.4 | 5.4 | 21.7
37.1 | 256.138 | 68.838 | Valve 4 at 30km | 187.3 |  |  | 0.4 | 0.9 | 3.7 | 14.7
37.2 | 266.8882 | 79.4882 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 0.9 | 3.7 | 15
37.3 | 286.9511 | 99.5511 | Valve 4 at 30km | 187.4 |  |  | 0.6 | 1.4 | 5.8 | 23.2
37.4 | 252.1751 | 64.7751 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 1.1 | 4.2 | 16.9
37.5 | 256.1878 | 68.7878 | Valve 4 at 30km | 187.4 |  |  | 0.4 | 1 | 3.9 | 15.6
37.6 | 277.538 | 90.238 | Valve 4 at 30km | 187.3 |  |  | 0.9 | 2.3 | 9.1 | 36.4
37.7 | 282.8882 | 95.5882 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.3 | 5.1 | 20.5
37.8 | 272.1878 | 84.8878 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.3 | 5.2 | 20.6
37.9 | 268.1751 | 80.8751 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.6 | 6.5 | 25.8
38 | 272.1878 | 84.8878 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.4 | 5.6 | 22.5
38.1 | 272.1878 | 84.8878 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.4 | 5.5 | 22.1
38.2 | 268.1751 | 80.8751 | Valve 4 at 30km | 187.3 |  |  | 0.8 | 1.8 | 7.3 | 29.1
38.3 | 272.1878 | 84.8878 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.4 | 5.8 | 23.1
38.4 | 277.538 | 90.238 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.3 | 5.2 | 20.9
38.5 | 292.3008 | 104.9008 | Valve 4 at 30km | 187.4 |  |  | 0.6 | 1.4 | 5.6 | 22.2
38.6 | 273.5751 | 86.1751 | Valve 4 at 30km | 187.4 |  |  | 0.7 | 1.6 | 6.3 | 25.1
38.7 | 277.5878 | 90.1878 | Valve 4 at 30km | 187.4 |  |  | 0.6 | 1.4 | 5.5 | 21.9
38.8 | 282.938 | 95.538 | Valve 4 at 30km | 187.4 |  |  | 0.5 | 1.2 | 4.6 | 18.5
38.9 | 293.5882 | 106.2882 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.3 | 5.3 | 21.1
39 | 278.8751 | 91.5751 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.3 | 5.3 | 21.2
39.1 | 282.8878 | 95.5878 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.2 | 4.7 | 18.7
39.2 | 302.9506 | 115.6506 | Valve 4 at 30km | 187.3 |  |  | 0.8 | 1.8 | 7.2 | 28.7
39.3 | 289.5751 | 102.2751 | Valve 4 at 30km | 187.3 |  |  | 0.9 | 2.1 | 8.5 | 33.9
39.4 | 293.5878 | 106.2878 | Valve 4 at 30km | 187.3 |  |  | 0.8 | 1.9 | 7.4 | 29.7
39.5 | 298.938 | 111.638 | Valve 4 at 30km | 187.3 |  |  | 0.7 | 1.7 | 6.7 | 26.6
39.6 | 313.6511 | 126.3511 | Valve 4 at 30km | 187.3 |  |  | 0.6 | 1.5 | 5.9 | 23.4
39.7 | 293.5878 | 106.2878 | Valve 4 at 30km | 187.3 |  |  | 0.8 | 1.8 | 7.2 | 28.7
39.8 | 278.8751 | 91.5751 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.1 | 4.5 | 17.9
39.9 | 282.8878 | 95.5878 | Valve 4 at 30km | 187.3 |  |  | 0.5 | 1.1 | 4.4 | 17.6
40 | 293.638 | 106.238 | Valve 4 at 30km | 187.4 |  |  | 0.6 | 1.4 | 5.5 | 22.1
40.1 | 304.2882 | 116.9882 | Valve 4 at 30km | 187.3 |  |  | 0.8 | 1.8 | 7 | 28.1
40.2 | 309.6384 | 122.3384 | Valve 4 at 30km | 187.3 |  |  | 0.7 | 1.5 | 6 | 24.2
40.3 | 331.0886 | 143.6886 | Valve 4 at 30km | 187.4 |  |  | 1.5 | 3.3 | 13.3 | 53.3
40.4 | 336.4388 | 149.0388 | Valve 4 at 30km | 187.4 |  |  | 1.2 | 2.6 | 10.5 | 42.2
40.5 | 347.089 | 159.789 | Valve 4 at 30km | 187.3 |  |  | 1.2 | 2.6 | 10.4 | 41.8
40.6 | 361.8021 | 174.5021 | Valve 4 at 30km | 187.3 |  |  | 0.9 | 2 | 8.2 | 32.7
40.7 | 314.9878 | 127.6878 | Valve 4 at 30km | 187.3 |  |  | 1 | 2.2 | 8.8 | 35.2
40.8 | 310.9751 | 123.6751 | Valve 4 at 30km | 187.3 |  |  | 1.2 | 2.7 | 10.9 | 43.5
40.9 | 324.3506 | 137.0506 | Valve 4 at 30km | 187.3 |  |  | 0.9 | 2 | 8 | 31.9
41 | 314.9878 | 127.6878 | Valve 4 at 30km | 187.3 |  |  | 1.2 | 2.6 | 10.4 | 41.5
41.1 | 305.6751 | 118.2751 | Valve 4 at 30km | 187.4 |  |  | 1.4 | 2.8 | 11.3 | 45.2
41.2 | 315.038 | 127.638 | Valve 4 at 30km | 187.4 |  |  | 1.5 | 2.9 | 11.8 | 47.1
41.3 | 298.9878 | 111.5878 | Valve 4 at 30km | 187.4 |  |  | 1 | 2 | 7.8 | 31.4
41.4 | 289.5751 | 102.2751 | Valve 4 at 30km | 187.3 |  |  | 1.1 | 2 | 7.9 | 31.6
41.5 | 298.9878 | 111.5878 | Valve 4 at 30km | 187.4 |  |  | 1 | 1.9 | 7.7 | 30.7
41.6 | 324.3506 | 137.0506 | Valve 4 at 30km | 187.3 |  |  | 1.1 | 2.3 | 9.1 | 36.2
41.7 | 300.2751 | 112.9751 | Valve 4 at 30km | 187.3 |  |  | 1.5 | 2.8 | 11.3 | 45.1
41.8 | 315.038 | 127.638 | Valve 4 at 30km | 187.4 |  |  | 1.8 | 3.9 | 15.8 | 63.1
41.9 | 288.2878 | 100.8878 | Valve 4 at 30km | 187.4 |  |  | 0.7 | 1.4 | 5.5 | 21.8
42 | 284.2751 | 96.8751 | Valve 4 at 30km | 187.4 |  |  | 0.8 | 1.4 | 5.7 | 22.8
42.1 | 293.5878 | 106.2878 | Valve 4 at 30km | 187.3 |  |  | 1.3 | 2.5 | 10 | 39.9
42.2 | 289.5751 | 102.2751 | Valve 4 at 30km | 187.3 |  |  | 1.3 | 2.6 | 10.4 | 41.6
42.3 | 345.7515 | 158.4515 | Valve 4 at 30km | 187.3 |  |  | 1.1 | 2 | 8.2 | 32.7
42.4 | 336.3886 | 149.0886 | Valve 4 at 30km | 187.3 |  |  | 1.4 | 2.6 | 10.6 | 42.4
42.5 | 309.6384 | 122.3384 | Valve 4 at 30km | 187.3 |  |  | 1 | 1.7 | 7 | 27.8
42.6 | 304.2882 | 116.9882 | Valve 4 at 30km | 187.3 |  |  | 1.3 | 2.9 | 11.8 | 47.1
42.7 | 293.638 | 106.238 | Valve 4 at 30km | 187.4 |  |  | 0.8 | 1.4 | 5.6 | 22.4
42.8 | 288.2878 | 100.8878 | Valve 4 at 30km | 187.4 |  |  | 0.9 | 1.5 | 5.8 | 23.4
42.9 | 278.8751 | 91.5751 | Valve 4 at 30km | 187.3 |  |  | 0.7 | 1.1 | 4.5 | 18
43 | 293.5878 | 106.2878 | Valve 4 at 30km | 187.3 |  |  | 0.9 | 1.5 | 6.2 | 24.7
43.1 | 315.038 | 127.638 | Valve 4 at 30km | 187.4 |  |  | 1.1 | 2 | 8 | 32
43.2 | 331.0882 | 143.6882 | Valve 4 at 30km | 187.4 |  |  | 1.5 | 2.7 | 10.6 | 42.5
43.3 | 352.4384 | 165.1384 | Valve 4 at 30km | 187.3 |  |  | 1.7 | 3.1 | 12.6 | 50.4
43.4 | 373.8886 | 186.4886 | Valve 4 at 30km | 187.4 |  |  | 2 | 5.4 | 21.7 | 86.7
43.5 | 384.5388 | 197.2388 | Valve 4 at 30km | 187.3 |  |  | 1.4 | 2.7 | 11 | 44
43.6 | 410.0017 | 222.6017 | Valve 4 at 30km | 187.4 |  |  | 1.5 | 3 | 11.8 | 47.3
43.7 | 364.4751 | 177.1751 | Valve 4 at 30km | 187.3 |  |  | 1.9 | 8.7 | 34.7 | 138.7
43.8 | 373.838 | 186.538 | Valve 4 at 30km | 187.3 |  |  | 1.9 | 5.2 | 21 | 83.8
43.9 | 363.1878 | 175.7878 | Valve 4 at 30km | 187.4 |  |  | 1.6 | 3 | 11.9 | 47.5
44 | 353.7751 | 166.4751 | Valve 4 at 30km | 187.3 |  |  | 1.5 | 2.8 | 11.4 | 45.5
44.1 | 363.1878 | 175.7878 | Valve 4 at 30km | 187.4 |  |  | 1.5 | 2.7 | 11 | 43.8
44.2 | 379.238 | 191.838 | Valve 4 at 30km | 187.4 |  |  | 1.7 | 3.4 | 13.6 | 54.6
44.3 | 389.8882 | 202.5882 | Valve 4 at 30km | 187.3 |  |  | 1.7 | 3.4 | 13.8 | 55
44.4 | 379.1878 | 191.8878 | Valve 4 at 30km | 187.3 |  |  | 1.7 | 3.6 | 14.3 | 57.2
44.5 | 369.8751 | 182.4751 | Valve 4 at 30km | 187.4 |  |  | 1.7 | 3.2 | 12.6 | 50.5
44.6 | 373.8878 | 186.4878 | Valve 4 at 30km | 187.4 |  |  | 1.7 | 3 | 12.1 | 48.4
44.7 | 384.538 | 197.238 | Valve 4 at 30km | 187.3 |  |  | 1.7 | 3.2 | 13 | 51.8
44.8 | 393.9008 | 206.6008 | Valve 4 at 30km | 187.3 |  |  | 1.5 | 2.9 | 11.4 | 45.8
44.9 | 375.1751 | 187.8751 | Valve 4 at 30km | 187.3 |  |  | 1.6 | 3 | 11.9 | 47.8
45 | 379.1878 | 36.6878 | Valve 4 at 30km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
45.1 | 389.938 | 42.038 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
45.2 | 399.3008 | 51.4008 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
45.3 | 380.5751 | 32.6751 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
45.4 | 393.9506 | 46.0506 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
45.5 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
45.6 | 364.4751 | 32.6751 | Valve 5 at 45km | 331.8 |  |  | 0 | 0.1 | 0.5 | 1
45.7 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
45.8 | 389.938 | 42.038 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
45.9 | 395.2882 | 47.3882 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46 | 400.6384 | 52.7384 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.1 | 380.5751 | 32.6751 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.2 | 380.5751 | 32.6751 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.3 | 384.5878 | 36.6878 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.4 | 399.3008 | 51.4008 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.5 | 384.5878 | 36.6878 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.6 | 375.1751 | 32.6751 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
46.7 | 384.5878 | 36.6878 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
46.8 | 395.238 | 42.038 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
46.9 | 426.0013 | 62.1013 | Valve 5 at 45km | 363.9 |  |  | 0 | 0.1 | 0.5 | 1
47 | 395.238 | 42.038 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
47.1 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
47.2 | 369.8751 | 32.6751 | Valve 5 at 45km | 337.2 |  |  | 0 | 0.1 | 0.5 | 1
47.3 | 375.1751 | 32.6751 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
47.4 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
47.5 | 389.938 | 42.038 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
47.6 | 380.5751 | 32.6751 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
47.7 | 384.5878 | 36.6878 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
47.8 | 389.938 | 42.038 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
47.9 | 380.5751 | 32.6751 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
48 | 399.2506 | 46.0506 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
48.1 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
48.2 | 375.1751 | 32.6751 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
48.3 | 379.1878 | 36.6878 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
48.4 | 384.538 | 42.038 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
48.5 | 395.2882 | 47.3882 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
48.6 | 405.9384 | 52.7384 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
48.7 | 411.2886 | 58.0886 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
48.8 | 385.8751 | 32.6751 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
48.9 | 416.6388 | 63.4388 | Valve 5 at 45km | 353.2 |  |  | 0 | 0.1 | 0.5 | 1
49 | 405.9886 | 58.0886 | Valve 5 at 45km | 347.9 |  |  | 0 | 0.1 | 0.5 | 1
49.1 | 395.2384 | 52.7384 | Valve 5 at 45km | 342.5 |  |  | 0 | 0.1 | 0.5 | 1
49.2 | 379.1882 | 47.3882 | Valve 5 at 45km | 331.8 |  |  | 0 | 0.1 | 0.5 | 1
49.3 | 368.538 | 42.038 | Valve 5 at 45km | 326.5 |  |  | 0 | 0.1 | 0.5 | 1
49.4 | 363.1878 | 36.6878 | Valve 5 at 45km | 326.5 |  |  | 0 | 0.1 | 0.5 | 1
49.5 | 353.7751 | 32.6751 | Valve 5 at 45km | 321.1 |  |  | 0 | 0.1 | 0.5 | 1
49.6 | 357.7878 | 36.6878 | Valve 5 at 45km | 321.1 |  |  | 0 | 0.1 | 0.5 | 1
49.7 | 353.7751 | 32.6751 | Valve 5 at 45km | 321.1 |  |  | 0 | 0.1 | 0.5 | 1
49.8 | 383.2511 | 56.7511 | Valve 5 at 45km | 326.5 |  |  | 0 | 0.1 | 0.5 | 1
49.9 | 368.4882 | 47.3882 | Valve 5 at 45km | 321.1 |  |  | 0 | 0.1 | 0.5 | 1
50 | 411.338 | 42.038 | Valve 5 at 45km | 369.3 |  |  | 0 | 0.1 | 0.5 | 1

## Drain Down Times
Typical Pipeline - Time to Drain Down
VACUUM DRAIN-DOWN | Block Valves Closed
Pipeline rupture | 0 | hours
50 mm (2 inch diameter) large hole | 0.1 | hours
25 mm (1 inch diameter) medium hole | 0.5 | hours
12.5 mm (half inch diameter) small hole | 1 | hours
Amount Draining Down | 47.3882 | m3
Leak Distance from Point A | 34 | km

## Chainage & Names
Quick Look-Up Tables to find locations and chainage
Chainage Listing |  | Alphabetical Listing
USE SLIDER BAR >>>
Distance from Point A | Description | Description | Distance from Point A
0.1 | Rail Crossing 01 | A1 | 8.4
0.3 | Roadl Crossing | A2 | 17.6
0.6 | Rail Crossing | A3 | 1
1 | Major Road | A Village | 4.2
0 to 2 | Village | B Village | 45
2.2 | Stream | C road | 32
2 to 4 | Town | C town | 16.4
3.9 | Major Road | Rail Crossing 01 | 0.1
4.2 | Major Road | Rail Crossing 02 | 0.6
4 to 5 | Village XXX | Rail Crossing near village XXX | 5.1
5.1 | Rail Crossing near village XXX | Rail Crossing 03 | 7
6.5 | River | Rail Crossing 04 | 10.2
7 to 8 | Village | Rail Crossing 05 | 15.5
7.8 | Minor road | Major Road | 1
8 to 10 | Village | Major Road | 3.9
8.4 | Major Road | etc
8.5 to 10.5 | Village | etc
10.6 | etc | etc
10.5 to 13.4 | etc
12.3 | etc

## Profile
Height Profile
Length km | database | Datapoints | 500
Pipeline ID mm | 261
Density kg/m3 | 800 | Pipeline Profile
| No | Chainage from Pumps- km | Height above sea level - metres
| 1 | 0 | 8.54
| 2 | 0.1 | 7.23
| 3 | 0.2 | 6.11
| 4 | 0.3 | 5.33
| 5 | 0.4 | 4.47
| 6 | 0.5 | 4.42
| 7 | 0.6 | 4.81
| 8 | 0.7 | 5.05
| 9 | 0.8 | 5.03
| 10 | 0.9 | 6.68
| 11 | 1 | 7.15
| 12 | 1.1 | 5.72
| 13 | 1.2 | 5.73
| 14 | 1.3 | 5.75
| 15 | 1.4 | 5.33
| 16 | 1.5 | 7.86
| 17 | 1.6 | 4.84
| 18 | 1.7 | 2.47
| 19 | 1.8 | 2.45
| 20 | 1.9 | 1.78 |  | Block Valves
| 21 | 2 | 1.71 |  | Number of Valves | chainage | elevation
| 22 | 2.1 | 1.97 |  | 5 | km | m
| 23 | 2.2 | 1.02 |  | Valve 1 at 10km | 10 | 27.17
| 24 | 2.3 | 1.36 |  | Valve 2 at 15km | 15 | 127.14
| 25 | 2.4 | 1.41 |  | Valve 3 at 26km | 26 | 155.5
| 26 | 2.5 | 2.94 |  | Valve 4 at 30km | 30 | 42.44
| 27 | 2.6 | 3.4 |  | Valve 5 at 45km | 45 | 8.23
| 28 | 2.7 | 2.56
| 29 | 2.8 | 1.8 | Contact rodmcconnell@btinternet.com for further details
| 30 | 2.9 | 2.46
| 31 | 3 | 3.32
| 32 | 3.1 | 3.77
| 33 | 3.2 | 4.38
| 34 | 3.3 | 5.76
| 35 | 3.4 | 7.18
| 36 | 3.5 | 8.81
| 37 | 3.6 | 8.37
| 38 | 3.7 | 9.33
| 39 | 3.8 | 9.61
| 40 | 3.9 | 9.52
| 41 | 4 | 10.16
| 42 | 4.1 | 10.02
| 43 | 4.2 | 6.17
| 44 | 4.3 | 8.42
| 45 | 4.4 | 8.92
| 46 | 4.5 | 9.33
| 47 | 4.6 | 9.76
| 48 | 4.7 | 10.95
| 49 | 4.8 | 11.02
| 50 | 4.9 | 12.14
| 51 | 5 | 14.23
| 52 | 5.1 | 11.91
| 53 | 5.2 | 16.06
| 54 | 5.3 | 16.08
| 55 | 5.4 | 16.35
| 56 | 5.5 | 17.65
| 57 | 5.6 | 14.16
| 58 | 5.7 | 13.18
| 59 | 5.8 | 12.39
| 60 | 5.9 | 14.11
| 61 | 6 | 14.26
| 62 | 6.1 | 13.35
| 63 | 6.2 | 11.32
| 64 | 6.3 | 10.64
| 65 | 6.4 | 10.87
| 66 | 6.5 | 11.39
| 67 | 6.6 | 12.32
| 68 | 6.7 | 16.13
| 69 | 6.8 | 18.83
| 70 | 6.9 | 20.98
| 71 | 7 | 23.07
| 72 | 7.1 | 24.32
| 73 | 7.2 | 26.26
| 74 | 7.3 | 28.06
| 75 | 7.4 | 29.39
| 76 | 7.5 | 29.82
| 77 | 7.6 | 30.52
| 78 | 7.7 | 32.85
| 79 | 7.8 | 32.06
| 80 | 7.9 | 30.81
| 81 | 8 | 29.53
| 82 | 8.1 | 28.25
| 83 | 8.2 | 24.23
| 84 | 8.3 | 20.82
| 85 | 8.4 | 20.32
| 86 | 8.5 | 22.18
| 87 | 8.6 | 26.25
| 88 | 8.7 | 28.54
| 89 | 8.8 | 30.69
| 90 | 8.9 | 30.17
| 91 | 9 | 30.97
| 92 | 9.1 | 33.6
| 93 | 9.2 | 34.91
| 94 | 9.3 | 34.42
| 95 | 9.4 | 32.73
| 96 | 9.5 | 29.3
| 97 | 9.6 | 30.26
| 98 | 9.7 | 35.15
| 99 | 9.8 | 33.79
| 100 | 9.9 | 31.71
| 101 | 10 | 27.17
| 102 | 10.1 | 29.63
| 103 | 10.2 | 32.58
| 104 | 10.3 | 34.85
| 105 | 10.4 | 35.53
| 106 | 10.5 | 29.08
| 107 | 10.6 | 31.1
| 108 | 10.7 | 34.42
| 109 | 10.8 | 36.21
| 110 | 10.9 | 39.1
| 111 | 11 | 41.79
| 112 | 11.1 | 42.27
| 113 | 11.2 | 39.03
| 114 | 11.3 | 37.88
| 115 | 11.4 | 39.73
| 116 | 11.5 | 39.51
| 117 | 11.6 | 41.39
| 118 | 11.7 | 44.78
| 119 | 11.8 | 46.22
| 120 | 11.9 | 46.14
| 121 | 12 | 45.32
| 122 | 12.1 | 45.27
| 123 | 12.2 | 46.32
| 124 | 12.3 | 47.63
| 125 | 12.4 | 51.36
| 126 | 12.5 | 55.97
| 127 | 12.6 | 59.67
| 128 | 12.7 | 62.8
| 129 | 12.8 | 65.36
| 130 | 12.9 | 66.99
| 131 | 13 | 68.83
| 132 | 13.1 | 70.49
| 133 | 13.2 | 72.27
| 134 | 13.3 | 75.91
| 135 | 13.4 | 79.48
| 136 | 13.5 | 81.83
| 137 | 13.6 | 82.8
| 138 | 13.7 | 83.41
| 139 | 13.8 | 85.08
| 140 | 13.9 | 87.89
| 141 | 14 | 90.06
| 142 | 14.1 | 93.42
| 143 | 14.2 | 96.37
| 144 | 14.3 | 99.55
| 145 | 14.4 | 102.82
| 146 | 14.5 | 106.38
| 147 | 14.6 | 110.45
| 148 | 14.7 | 115.44
| 149 | 14.8 | 119.51
| 150 | 14.9 | 123.13
| 151 | 15 | 127.14
| 152 | 15.1 | 130.66
| 153 | 15.2 | 132.61
| 154 | 15.3 | 134.37
| 155 | 15.4 | 135.05
| 156 | 15.5 | 135.83
| 157 | 15.6 | 135.91
| 158 | 15.7 | 134
| 159 | 15.8 | 134.41
| 160 | 15.9 | 134.89
| 161 | 16 | 135.42
| 162 | 16.1 | 135.35
| 163 | 16.2 | 135.38
| 164 | 16.3 | 135.83
| 165 | 16.4 | 135.52
| 166 | 16.5 | 134.17
| 167 | 16.6 | 132.7
| 168 | 16.7 | 133.09
| 169 | 16.8 | 132.56
| 170 | 16.9 | 132.03
| 171 | 17 | 131.43
| 172 | 17.1 | 131.49
| 173 | 17.2 | 132.05
| 174 | 17.3 | 134.44
| 175 | 17.4 | 136.37
| 176 | 17.5 | 137.83
| 177 | 17.6 | 137.51
| 178 | 17.7 | 138.92
| 179 | 17.8 | 139.01
| 180 | 17.9 | 139.49
| 181 | 18 | 138.57
| 182 | 18.1 | 137.3
| 183 | 18.2 | 136.78
| 184 | 18.3 | 136.49
| 185 | 18.4 | 136.87
| 186 | 18.5 | 136.18
| 187 | 18.6 | 137.18
| 188 | 18.7 | 137.71
| 189 | 18.8 | 138.54
| 190 | 18.9 | 139.48
| 191 | 19 | 140.45
| 192 | 19.1 | 140.57
| 193 | 19.2 | 140.79
| 194 | 19.3 | 141.4
| 195 | 19.4 | 142.14
| 196 | 19.5 | 142.86
| 197 | 19.6 | 143.68
| 198 | 19.7 | 144.43
| 199 | 19.8 | 144.86
| 200 | 19.9 | 145.3
| 201 | 20 | 145.81
| 202 | 20.1 | 146.28
| 203 | 20.2 | 146.91
| 204 | 20.3 | 147.02
| 205 | 20.4 | 147.63
| 206 | 20.5 | 147.84
| 207 | 20.6 | 148.73
| 208 | 20.7 | 148.78
| 209 | 20.8 | 148.87
| 210 | 20.9 | 148.91
| 211 | 21 | 149.33
| 212 | 21.1 | 150
| 213 | 21.2 | 150.89
| 214 | 21.3 | 151.71
| 215 | 21.4 | 152.29
| 216 | 21.5 | 152.36
| 217 | 21.6 | 152.64
| 218 | 21.7 | 152.33
| 219 | 21.8 | 152
| 220 | 21.9 | 154.89
| 221 | 22 | 157.14
| 222 | 22.1 | 157.9
| 223 | 22.2 | 158.16
| 224 | 22.3 | 156.83
| 225 | 22.4 | 153.89
| 226 | 22.5 | 155.47
| 227 | 22.6 | 156.95
| 228 | 22.7 | 157.26
| 229 | 22.8 | 157.16
| 230 | 22.9 | 155.86
| 231 | 23 | 154.92
| 232 | 23.1 | 155.95
| 233 | 23.2 | 156.05
| 234 | 23.3 | 155.49
| 235 | 23.4 | 154.79
| 236 | 23.5 | 153.86
| 237 | 23.6 | 153.13
| 238 | 23.7 | 151.11
| 239 | 23.8 | 154.16
| 240 | 23.9 | 156.29
| 241 | 24 | 157.68
| 242 | 24.1 | 158.76
| 243 | 24.2 | 159.05
| 244 | 24.3 | 159.58
| 245 | 24.4 | 160.02
| 246 | 24.5 | 160.23
| 247 | 24.6 | 159.81
| 248 | 24.7 | 159.15
| 249 | 24.8 | 158.4
| 250 | 24.9 | 157.93
| 251 | 25 | 157.73
| 252 | 25.1 | 157.47
| 253 | 25.2 | 157.92
| 254 | 25.3 | 157.49
| 255 | 25.4 | 156.81
| 256 | 25.5 | 155.97
| 257 | 25.6 | 154.89
| 258 | 25.7 | 155.26
| 259 | 25.8 | 156.67
| 260 | 25.9 | 156.61
| 261 | 26 | 155.5
| 262 | 26.1 | 152.2
| 263 | 26.2 | 149.14
| 264 | 26.3 | 146.22
| 265 | 26.4 | 144.31
| 266 | 26.5 | 142.31
| 267 | 26.6 | 139.9
| 268 | 26.7 | 138.37
| 269 | 26.8 | 136.38
| 270 | 26.9 | 133.05
| 271 | 27 | 128.43
| 272 | 27.1 | 125.53
| 273 | 27.2 | 121.96
| 274 | 27.3 | 117.41
| 275 | 27.4 | 115.1
| 276 | 27.5 | 109.74
| 277 | 27.6 | 102.19
| 278 | 27.7 | 89.3
| 279 | 27.8 | 86.11
| 280 | 27.9 | 74.07
| 281 | 28 | 61.09
| 282 | 28.1 | 54.01
| 283 | 28.2 | 50.78
| 284 | 28.3 | 51.44
| 285 | 28.4 | 52.65
| 286 | 28.5 | 54.7
| 287 | 28.6 | 53.09
| 288 | 28.7 | 49.29
| 289 | 28.8 | 48.3
| 290 | 28.9 | 46.4
| 291 | 29 | 44.03
| 292 | 29.1 | 41.48
| 293 | 29.2 | 39.82
| 294 | 29.3 | 38.74
| 295 | 29.4 | 37.98
| 296 | 29.5 | 36.76
| 297 | 29.6 | 37.03
| 298 | 29.7 | 37.87
| 299 | 29.8 | 40.56
| 300 | 29.9 | 40.71
| 301 | 30 | 42.44
| 302 | 30.1 | 42.54
| 303 | 30.2 | 41.89
| 304 | 30.3 | 41.72
| 305 | 30.4 | 41.34
| 306 | 30.5 | 41.58
| 307 | 30.6 | 42.23
| 308 | 30.7 | 42.72
| 309 | 30.8 | 39.15
| 310 | 30.9 | 39.47
| 311 | 31 | 39.69
| 312 | 31.1 | 39.45
| 313 | 31.2 | 39.81
| 314 | 31.3 | 40.4
| 315 | 31.4 | 41.46
| 316 | 31.5 | 41.95
| 317 | 31.6 | 41.96
| 318 | 31.7 | 42.2
| 319 | 31.8 | 43.31
| 320 | 31.9 | 42.95
| 321 | 32 | 44.06
| 322 | 32.1 | 43.9
| 323 | 32.2 | 42.04
| 324 | 32.3 | 42.91
| 325 | 32.4 | 46.27
| 326 | 32.5 | 47.73
| 327 | 32.6 | 45.67
| 328 | 32.7 | 44.1
| 329 | 32.8 | 45.92
| 330 | 32.9 | 45.72
| 331 | 33 | 46.77
| 332 | 33.1 | 47.38
| 333 | 33.2 | 47.09
| 334 | 33.3 | 46.26
| 335 | 33.4 | 44.53
| 336 | 33.5 | 44.13
| 337 | 33.6 | 46.11
| 338 | 33.7 | 46.55
| 339 | 33.8 | 45.83
| 340 | 33.9 | 43.73
| 341 | 34 | 42.36
| 342 | 34.1 | 42.24
| 343 | 34.2 | 40.97
| 344 | 34.3 | 38.95
| 345 | 34.4 | 37.21
| 346 | 34.5 | 35.29
| 347 | 34.6 | 33.57
| 348 | 34.7 | 34.73
| 349 | 34.8 | 34.12
| 350 | 34.9 | 36.19
| 351 | 35 | 37.21
| 352 | 35.1 | 37.63
| 353 | 35.2 | 39.49
| 354 | 35.3 | 41.35
| 355 | 35.4 | 39.99
| 356 | 35.5 | 37.43
| 357 | 35.6 | 34.66
| 358 | 35.7 | 31.56
| 359 | 35.8 | 32.36
| 360 | 35.9 | 34.2
| 361 | 36 | 32.95
| 362 | 36.1 | 31.86
| 363 | 36.2 | 28.93
| 364 | 36.3 | 29.92
| 365 | 36.4 | 31.28
| 366 | 36.5 | 31.95
| 367 | 36.6 | 31.64
| 368 | 36.7 | 30.26
| 369 | 36.8 | 31.45
| 370 | 36.9 | 32.78
| 371 | 37 | 32.62
| 372 | 37.1 | 31.48
| 373 | 37.2 | 29.61
| 374 | 37.3 | 29.08
| 375 | 37.4 | 30.19
| 376 | 37.5 | 29.82
| 377 | 37.6 | 28.37
| 378 | 37.7 | 27.18
| 379 | 37.8 | 27.22
| 380 | 37.9 | 28.06
| 381 | 38 | 27.65
| 382 | 38.1 | 27.57
| 383 | 38.2 | 28.24
| 384 | 38.3 | 27.75
| 385 | 38.4 | 27.29
| 386 | 38.5 | 26.17
| 387 | 38.6 | 26.71
| 388 | 38.7 | 26.08
| 389 | 38.8 | 24.71
| 390 | 38.9 | 23.63
| 391 | 39 | 23.67
| 392 | 39.1 | 22.51
| 393 | 39.2 | 20.96
| 394 | 39.3 | 21.16
| 395 | 39.4 | 21.02
| 396 | 39.5 | 20.76
| 397 | 39.6 | 20.14
| 398 | 39.7 | 20.96
| 399 | 39.8 | 21.97
| 400 | 39.9 | 21.78
| 401 | 40 | 21.37
| 402 | 40.1 | 20.91
| 403 | 40.2 | 20.34
| 404 | 40.3 | 19.65
| 405 | 40.4 | 19.44
| 406 | 40.5 | 18.48
| 407 | 40.6 | 17.63
| 408 | 40.7 | 18.01
| 409 | 40.8 | 18.53
| 410 | 40.9 | 17.49
| 411 | 41 | 18.47
| 412 | 41.1 | 19.53
| 413 | 41.2 | 19.57
| 414 | 41.3 | 19.95
| 415 | 41.4 | 21.1
| 416 | 41.5 | 19.91
| 417 | 41.6 | 18.12
| 418 | 41.7 | 19.79
| 419 | 41.8 | 19.7
| 420 | 41.9 | 21.3
| 421 | 42 | 21.52
| 422 | 42.1 | 21.23
| 423 | 42.2 | 21.24
| 424 | 42.3 | 17.63
| 425 | 42.4 | 18.5
| 426 | 42.5 | 20.89
| 427 | 42.6 | 21.26
| 428 | 42.7 | 21.45
| 429 | 42.8 | 21.62
| 430 | 42.9 | 22.07
| 431 | 43 | 20.45
| 432 | 43.1 | 18.6
| 433 | 43.2 | 17.14
| 434 | 43.3 | 15.17
| 435 | 43.4 | 13.79
| 436 | 43.5 | 12.08
| 437 | 43.6 | 9.24
| 438 | 43.7 | 10.76
| 439 | 43.8 | 10.75
| 440 | 43.9 | 11.47
| 441 | 44 | 12.31
| 442 | 44.1 | 10.97
| 443 | 44.2 | 9.6
| 444 | 44.3 | 8.95
| 445 | 44.4 | 9.01
| 446 | 44.5 | 9.49
| 447 | 44.6 | 9.34
| 448 | 44.7 | 8.8
| 449 | 44.8 | 8.12
| 450 | 44.9 | 8.42
| 451 | 45 | 8.23
| 452 | 45.1 | 7.53
| 453 | 45.2 | 6.52
| 454 | 45.3 | 7.44
| 455 | 45.4 | 7.11
| 456 | 45.5 | 7.97
| 457 | 45.6 | 9.69
| 458 | 45.7 | 8.63
| 459 | 45.8 | 6.86
| 460 | 45.9 | 6.71
| 461 | 46 | 6.3
| 462 | 46.1 | 6.36
| 463 | 46.2 | 6.34
| 464 | 46.3 | 5.98
| 465 | 46.4 | 5.75
| 466 | 46.5 | 6.88
| 467 | 46.6 | 7.8
| 468 | 46.7 | 6.06
| 469 | 46.8 | 5.14
| 470 | 46.9 | 2.24
| 471 | 47 | 5.62
| 472 | 47.1 | 7.64
| 473 | 47.2 | 9.18
| 474 | 47.3 | 9.13
| 475 | 47.4 | 7.77
| 476 | 47.5 | 6.92
| 477 | 47.6 | 7.04
| 478 | 47.7 | 6.86
| 479 | 47.8 | 6.22
| 480 | 47.9 | 6.32
| 481 | 48 | 5.34
| 482 | 48.1 | 8.08
| 483 | 48.2 | 9.09
| 484 | 48.3 | 8.89
| 485 | 48.4 | 8.27
| 486 | 48.5 | 6.27
| 487 | 48.6 | 4.88
| 488 | 48.7 | 4.69
| 489 | 48.8 | 4.81
| 490 | 48.9 | 4.91
| 491 | 49 | 6.15
| 492 | 49.1 | 8.05
| 493 | 49.2 | 10.17
| 494 | 49.3 | 11.26
| 495 | 49.4 | 11.69
| 496 | 49.5 | 11.86
| 497 | 49.6 | 11.95
| 498 | 49.7 | 12.14
| 499 | 49.8 | 11.56
| 500 | 49.9 | 11.84