PREDICTION OF EXTERNAL INTERFERENCE FAILURE PROBABILITIES USING STRUCTURAL RELIABILITY ANALYSIS

BACKGROUND

The objective of the structural reliability analysis is to derive probabilities of failure for a range of pipeline cases using data recorded in the UKOPA fault database by participating pipeline operators.

The models make use of available data on damage (dents and gouges) that did not lead to a release of product from the affected pipeline. These data are much more numerous than data on product loss incidents and therefore more detailed analysis can be carried out.

This note describes the structural reliability analysis carried out to date.

EXTERNAL INTERFERENCE DATA

The UKOPA Fault Database contains records of 1006 gouges caused by external interference, 185 of which are associated with a dent. Of the 1006 gouges, 665 occurred on pipelines operating in Rural areas and 341 occurred on pipelines operating in Suburban, Semi-Rural or Urban areas (referred to collectively as Suburban areas for brevity).

The pipeline exposure recorded in the database totals 443447 km years for Rural area pipelines and 46578 km years for Suburban pipelines.

CALCULATION OF INCIDENT RATE

The incident rate for external interference, i.e. the rate at which new gouges occur on the pipeline system, depends on the area classification (Rural or Suburban). The incident rate is found by dividing the number of gouges in each area class by the exposure in that area class. Therefore,

Rural area incident rate = 665 / 443447 = 1.50 x10-3 / kmyr

Suburban area incident rate = 341 / 46578 = 7.32 x10-3 / kmyr

The data shows that the suburban area incident rate is approximately 5 times grater than the rural area rate.

CONSTRUCTION OF DAMAGE DISTRIBUTIONS

Gouge Length & Depth

The records of gouge length and gouge depth contained in the fault database have been used to derive statistical distributions of these quantities for use in the structural reliability analysis.

Denting Force

The records of dent depth contained in the fault database have been combined with the corresponding wall thickness, diameter, grade and operating pressure data to determine the force exerted on the pipeline to create the dent. A statistical distribution of this denting force has been derived for use in the structural reliability analysis.

From experience, the Weibull distribution has been chosen to represent each of the three quantities, and linear regression has been used to determine the parameters of each distribution. The analysis has shown that there is no significant difference between the distributions for gouges or dents in Rural or Suburban areas, and therefore the data has been pooled to derive an overall distribution for each quantity.

The Weibull distribution is defined by


[image: image1.wmf](

)

ú

ú

û

ù

ê

ê

ë

é

÷

÷

ø

ö

ç

ç

è

æ

b

-

-

=

a

x

exp

1

x

P


where P(x) is the cumulative distribution function and  and  are the parameters to be determined.

The cumulative probability data extracted from the fault database and the derived Weibull distributions are shown grahically in Figures 1 – 3. The parameters of the distributions for gouge depth, a, gouge length, L, and denting force, F, are given in Table 1 below.

Quantity
Units



Gouge Depth (a)
mm
0.63
0.73

Gouge Length (L)
mm
0.84
183.6

Denting Force (F)
kN
2.12
110.2

Table 1: Distribution Parameters

The distributions are shown in the form of probability density functions in Figures 4 – 6.

ANALYSIS RESULTS

Structural reliability analysis has been used to illustrate the dependence of failure probability on pipeline wall thickness.

Previous analysis of leak and rupture incident data from the database has determined overall failure frequencies due to external interference for broad wall thickness categories as shown in Table 2 below.

Wall Thickness

mm
Failure Frequency

per km year

< 5
2.37 x10-4

5 – 10
6.80 x10-5

10 – 15
2.08 x10-5

> 15
0

Table 2: Failure Frequencies from Leak Database

In order to demonstrate the benefits of structural reliability analysis, two notional pipelines have been assessed:

· 914 mm diameter, 75 bar

· 273 mm diameter, 98 bar

The probability of failure of each of these pipelines due to external interference has been calculated for a range of combinations of wall thickness and grade chosen to maintain a design factor of around 0.7.

The results of this analysis are shown in Figures 7 & 8.

DISCUSSION

The structural reliability analysis results shown in Figures 7 & 8 demonstrate that wall thickness has a strong influence on failure probability. Whereas leak data is so sparse that meaningful failure frequencies can only be derived for broad categories of wall thickness, structural reliability analysis enables the failure probability to be calculated for any value of wall thickness and therefore allows the effect of small changes in wall thickness to be determined.


[image: image2.wmf]Gouge Depth

0

0.2

0.4

0.6

0.8

1

0

2

4

6

8

10

a (mm)

P(a)

Data

Weibull Fit


Figure 1: Distribution of Gouge Depth Data


[image: image3.wmf]Gouge Length

0

0.2

0.4

0.6

0.8

1

0

500

1000

1500

2000

L (mm)

P(L)

Data

Weibull Fit


Figure 2: Distribution of Gouge Length Data


[image: image4.wmf]Denting Force

0

0.2

0.4

0.6

0.8

1

0

100

200

300

400

F (kN)

P(F)

Data

Weibull Fit


Figure 3: Distribution of Denting Force Data

[image: image5.wmf]Gouge Depth

0

0.2

0.4

0.6

0.8

1

1.2

1.4

0

1

2

3

4

5

6

7

8

a (mm)

P(a)


Figure 4: Probability Density Function for Gouge Depth


[image: image6.wmf]Gouge Length

0

0.002

0.004

0.006

0.008

0.01

0

200

400

600

800

1000

L (mm)

P(L)


Figure 5: Probability Density Function for Gouge Length


[image: image7.wmf]Denting Force

0

0.002

0.004

0.006

0.008

0.01

0

50

100

150

200

250

300

F (kN)

P(F)


Figure 6: Probability Density Function for Denting Force


[image: image8.wmf]914mm diameter, 75bar

0.E+00

1.E-05

2.E-05

3.E-05

4.E-05

5.E-05

6.E-05

7.E-05

8.E-05

9.E-05

8

10

12

14

16

18

Wall Thickness (mm)

Probability of Failure (per km year)

Model

Leak Data


Figure 7: Influence of Wall Thickness on Failure Probability


[image: image9.wmf]273mm diameter, 98bar

0.0E+00

5.0E-05

1.0E-04

1.5E-04

2.0E-04

2.5E-04

3.0E-04

3.5E-04

4

5

6

7

8

9

Wall Thickness (mm)

Probability of Failure (per km year)

Model

Leak Data


Figure 8: Influence of Wall Thickness on Failure Probability

_1035115035.xls
Chart3

		0		0

		33		33

		39		39

		40		40

		41		41

		42		42

		43		43

		47		47

		49		49

		52		52

		57		57

		61		61

		64		64

		66		66

		67		67

		68		68

		73		73

		74		74

		75		75

		77		77

		81		81

		86		86

		90		90

		96		96

		97		97

		98		98

		102		102

		103		103

		111		111

		112		112

		116		116

		117		117

		120		120

		122		122

		128		128

		130		130

		137		137

		149		149

		175		175

		190		190

		253		253

		339		339

		393		393



Data

Weibull Fit

F (kN)

P(F)

Denting Force

0

0

0.0126353791

0.0746593717

0.0306859206

0.1046751313

0.0667870036

0.1101171321

0.0848375451

0.1156791714

0.1028880866

0.1213590305

0.1209386282

0.1271544257

0.1570397112

0.1514435356

0.1750902527

0.164217522

0.2111913357

0.1841059778

0.2292418773

0.2190071828

0.2472924188

0.24829652

0.2833935018

0.2709349703

0.3014440433

0.2863007675

0.3375451264

0.2940563863

0.3916967509

0.3018563267

0.4097472924

0.3414117363

0.4277978339

0.3494122118

0.463898917

0.3574352807

0.5180505415

0.3735369758

0.536101083

0.4058781492

0.5541516245

0.4463204086

0.5722021661

0.4784667452

0.5902527076

0.5259448571

0.6083032491

0.5337398423

0.6624548736

0.541494946

0.6805054152

0.5720735457

0.6985559567

0.579597476

0.7346570397

0.6377616231

0.7527075812

0.6447540446

0.7707581227

0.6720435438

0.7888086643

0.6786897538

0.8068592058

0.6981881807

0.8249097473

0.7108109097

0.8429602888

0.7468060793

0.8610108303

0.7581647241

0.8790613718

0.7953463497

0.8971119134

0.8497608184

0.9151624549

0.930451232

0.9332129964

0.9581413687

0.9512635379

0.9970430189

0.9693140794

0.9999801885

0.9873646209

0.9999996318



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		



Data

Weibull Fit

L (mm)

P(L)

Gouge Length



		



Weibull Fit

L (mm)

P(L)

Gouge Length



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035115068.xls
Chart5

		0

		2

		3

		4

		5

		6

		7

		8

		9

		10

		11

		13

		14

		15

		16

		17

		19

		20

		21

		22

		23

		25

		28

		30

		32

		34

		35

		36

		38

		40

		42

		44

		45

		47

		50

		51

		54

		55

		57

		60

		62

		63

		64

		65

		68

		70

		73

		74

		75

		76

		80

		83

		85

		86

		89

		90

		95

		100

		102

		108

		110

		112

		113

		115

		119

		120

		125

		127

		130

		135

		137

		138

		139

		140

		149

		150

		152

		155

		160

		165

		168

		170

		171

		176

		178

		180

		187

		190

		200

		203

		205

		210

		220

		225

		229

		230

		235

		239

		240

		241

		247

		250

		254

		255

		256

		260

		267

		270

		275

		279

		290

		300

		305

		310

		312

		319

		320

		330

		335

		350

		353

		356

		359

		370

		380

		381

		400

		420

		425

		435

		450

		457

		479

		480

		483

		500

		502

		520

		528

		559

		570

		580

		585

		598

		600

		610

		635

		650

		685

		686

		710

		718

		740

		750

		762

		770

		838

		914

		920

		930

		1007

		1020

		1118

		1197

		1198

		1220

		1250

		1252

		1300

		1420

		1473

		1500

		1829

		2100

		2500

		3000

		3048

		7620

		9144



Weibull Fit

L (mm)

P(L)

Gouge Length

0.0092195903

0.0085621092

0.0081066977

0.0077578318

0.0074745917

0.0072357614

0.007028954

0.0068463216

0.0066825847

0.0065340246

0.0062722419

0.0061553996

0.0060461574

0.0059435215

0.0058466834

0.0056678449

0.0055848201

0.0055055032

0.0054295524

0.005356672

0.0052191253

0.0050303388

0.004914326

0.0048050388

0.0047016945

0.0046520438

0.0046036446

0.0045103458

0.0044213381

0.0043362283

0.0042546775

0.0042151434

0.0041383914

0.0040286166

0.0039933477

0.0038911882

0.0038582826

0.0037940812

0.0037015561

0.0036422162

0.0036132087

0.0035846261

0.0035564567

0.0034743175

0.00342143

0.0033447206

0.003319816

0.0032952309

0.0032709577

0.0031768446

0.0031092076

0.0030654315

0.0030439217

0.0029808451

0.002960288

0.0028608174

0.0027665091

0.0027301302

0.0026252729

0.0025916701

0.0025587068

0.0025424587

0.0025104177

0.0024480936

0.0024328663

0.0023587514

0.0023300138

0.0022878366

0.0022199098

0.0021935322

0.0021805076

0.0021675906

0.0021547798

0.0020440513

0.0020322336

0.0020088757

0.0019745166

0.0019189912

0.001865537

0.0018344122

0.0018140431

0.0018039704

0.0017546945

0.0017354778

0.0017165345

0.0016523093

0.0016257343

0.0015410114

0.0015166957

0.0015007546

0.0014618168

0.0013876695

0.0013523541

0.0013249008

0.0013181453

0.0012849977

0.0012592147

0.0012528683

0.0012465609

0.0012095204

0.0011915032

0.0011679843

0.0011621927

0.0011564358

0.0011337502

0.0010953267

0.0010793395

0.0010533106

0.001033026

0.000979595

0.0009338408

0.0009119105

0.0008905828

0.0008822159

0.0008536472

0.0008496548

0.0008109041

0.0007923011

0.0007393864

0.0007292993

0.0007193702

0.0007095962

0.0006750386

0.0006452845

0.0006423923

0.0005901464

0.0005402851

0.0005285744

0.0005059991

0.0004741354

0.0004600388

0.000418689

0.0004169103

0.0004116242

0.0003830384

0.0003798224

0.0003521843

0.000340619

0.0002995889

0.0002863584

0.0002748837

0.0002693354

0.000255473

0.0002534102

0.0002433644

0.0002200931

0.0002072967

0.0001804593

0.0001797499

0.0001635935

0.000158561

0.0001455594

0.0001400319

0.000133694

0.0001296397

0.0001000398

0.0000752539

0.0000735966

0.0000709196

0.0000534539

0.0000509842

0.0000358227

0.0000270704

0.0000269752

0.000024967

0.000022477

0.0000223205

0.0000188864

0.0000125007

0.0000104399

0.0000095289

0.0000032042

0.0000013413

0.0000003845

0.0000000847

0.0000000734

0

0



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		



Data

Weibull Fit

L (mm)

P(L)

Gouge Length



		



Weibull Fit

L (mm)

P(L)

Gouge Length



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035115111.xls
Chart1

		9		9

		9.5		9.5

		10		10

		10		10

		10.9		10.9

		11.9		11.9

		12.7		12.7

		14.3		14.3

		15		15

		15		15

		15.9		15.9

		17.5		17.5



Model

Leak Data

Wall Thickness (mm)

Probability of Failure (per km year)

914mm diameter, 75bar

0.000068

0.0000806

0.000068

0.000068

0.000068

0.000068

0.0000208

0.0000502

0.0000208

0.0000344

0.0000208

0.0000256

0.0000208

0.0000145

0.0000208

0.00000912

0.0000208

0.00000912

0

0.00000659

0

0.00000185

0



Sheet1

		

		wt		calc pf		calc pf		data

				914mm, 75bar		219mm, 49bar

		5.6						6.80E-05

		6						6.80E-05

		6.8						6.80E-05

		7.5						6.80E-05

		9						6.80E-05

		9.5		8.06E-05				6.80E-05

		10		6.80E-05				6.80E-05

		10		6.80E-05				2.08E-05

		10.9		5.02E-05				2.08E-05

		11.9		3.44E-05				2.08E-05

		12.7		2.56E-05				2.08E-05

		14.3		1.45E-05				2.08E-05

		15		9.12E-06				2.08E-05

		15		9.12E-06				0.00E+00

		15.9		6.59E-06				0.00E+00

		17.5		1.85E-06				0.00E+00





Sheet1

		



Model

Leak Data

Wall Thickness (mm)

Probability of Failure (per km year)

914mm diameter, 75bar



Sheet2

		





Sheet3

		






_1035717680.xls
Chart1

		4.5		4.5

		4.9		4.9

		5		5

		5		5

		5.3		5.3

		5.6		5.6

		6.3		6.3

		6.8		6.8

		8.4		8.4

		9		9



Model

Leak Data

Wall Thickness (mm)

Probability of Failure (per km year)

273mm diameter, 98bar

0.000237

0.000301

0.000237

0.000286

0.000237

0.000286

0.000068

0.000242

0.000068

0.000229

0.000068

0.000194

0.000068

0.000165

0.000068

0.000101

0.000068

0.000068



Sheet1

		

		wt		calc pf		calc pf		data

				914mm, 75bar		273mm, 98bar

		4.5						2.37E-04

		4.9				3.01E-04		2.37E-04

		5				2.86E-04		2.37E-04

		5				2.86E-04		6.80E-05

		5.3				2.42E-04		6.80E-05

		5.6				2.29E-04		6.80E-05

		6.3				1.94E-04		6.80E-05

		6.8				1.65E-04		6.80E-05

		8.4				1.01E-04		6.80E-05

		9						6.80E-05

		9.5		8.06E-05				6.80E-05

		10		6.80E-05				6.80E-05

		10		6.80E-05				2.08E-05

		10.9		5.02E-05				2.08E-05

		11.9		3.44E-05				2.08E-05

		12.7		2.56E-05				2.08E-05

		14.3		1.45E-05				2.08E-05

		15		9.12E-06				2.08E-05

		15		9.12E-06				0.00E+00

		15.9		6.59E-06				0.00E+00

		17.5		1.85E-06				0.00E+00





Sheet1

		



Model

Leak Data

Wall Thickness (mm)

Probability of Failure (per km year)

914mm diameter, 75bar



Sheet2

		



Model

Leak Data

Wall Thickness (mm)

Probability of Failure (per km year)

273mm diameter, 98bar



Sheet3

		





		






_1035115082.xls
Chart6

		0

		33

		39

		40

		41

		42

		43

		47

		49

		52

		57

		61

		64

		66

		67

		68

		73

		74

		75

		77

		81

		86

		90

		96

		97

		98

		102

		103

		111

		112

		116

		117

		120

		122

		128

		130

		137

		149

		175

		190

		253

		339

		393



Weibull Fit

F (kN)

P(F)

Denting Force

0

0.0046126247

0.0053812589

0.0055023843

0.0056213245

0.0057380131

0.005852386

0.0062855202

0.0064866991

0.0067681251

0.0071802201

0.0074563598

0.0076313034

0.0077324179

0.0077782997

0.0078210609

0.0079881548

0.0080122836

0.0080333441

0.0080663291

0.0080963566

0.008068776

0.0079973204

0.007814182

0.0077754141

0.0077344282

0.007549396

0.0074981459

0.0070253356

0.0069592784

0.0066822084

0.0066100329

0.0063874883

0.0062347034

0.0057602233

0.0055981829

0.00502409

0.0040519372

0.0022459648

0.0014821765

0.000144296

0.0000013417

0.0000000294



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		



Data

Weibull Fit

L (mm)

P(L)

Gouge Length



		



Weibull Fit

L (mm)

P(L)

Gouge Length



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035115053.xls
Chart4

		0

		0.1

		0.14

		0.2

		0.3

		0.4

		0.48

		0.5

		0.6

		0.7

		0.8

		0.9

		0.97

		1

		1.1

		1.2

		1.3

		1.4

		1.5

		1.6

		1.7

		1.8

		1.9

		2

		2.1

		2.2

		2.3

		2.4

		2.5

		2.6

		2.7

		2.8

		2.9

		3

		3.2

		3.3

		3.4

		3.5

		3.6

		3.7

		3.9

		4

		4.1

		4.4

		4.8

		5

		5.6

		6

		6.3

		6.4

		7

		7.1

		8

		9.5

		10.3

		12

		12.7

		15.2



Weibull Fit

a (mm)

P(a)

Gouge Depth

1.3530476833

1.116696584

0.8952834282

0.6774818322

0.5437373905

0.4676333891

0.4515004433

0.3834532524

0.3309768236

0.2892140277

0.25518466

0.2348960081

0.2269429696

0.2031568977

0.1828797464

0.1654179989

0.1502507313

0.1369783424

0.1252887538

0.1149344438

0.1057164319

0.0974728546

0.0900706542

0.083399424

0.0773667803

0.071894832

0.0669174537

0.0623781561

0.058228404

0.0544262761

0.0509353873

0.0477240158

0.0447643897

0.0395056195

0.0371658911

0.034995998

0.0329808749

0.0311070687

0.0293625343

0.0262191193

0.0248017406

0.0234763988

0.0199840925

0.0162487654

0.0146960571

0.0109892142

0.0091251281

0.0079669246

0.0076194801

0.005867946

0.0056235552

0.0038786234

0.0021709466

0.00161946

0.0008960536

0.0007097165

0.0003217021



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		



Data

Weibull Fit

L (mm)

P(L)

Gouge Length



		



Weibull Fit

L (mm)

P(L)

Gouge Length



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035114993.xls
Chart1

		0		0

		0.1		0.1

		0.14		0.14

		0.2		0.2

		0.3		0.3

		0.4		0.4

		0.48		0.48

		0.5		0.5

		0.6		0.6

		0.7		0.7

		0.8		0.8

		0.9		0.9

		0.97		0.97

		1		1

		1.1		1.1

		1.2		1.2

		1.3		1.3

		1.4		1.4

		1.5		1.5

		1.6		1.6

		1.7		1.7

		1.8		1.8

		1.9		1.9

		2		2

		2.1		2.1

		2.2		2.2

		2.3		2.3

		2.4		2.4

		2.5		2.5

		2.6		2.6

		2.7		2.7

		2.8		2.8

		2.9		2.9

		3		3

		3.2		3.2

		3.3		3.3

		3.4		3.4

		3.5		3.5

		3.6		3.6

		3.7		3.7

		3.9		3.9

		4		4

		4.1		4.1

		4.4		4.4

		4.8		4.8

		5		5

		5.6		5.6

		6		6

		6.3		6.3

		6.4		6.4

		7		7

		7.1		7.1

		8		8

		9.5		9.5

		10.3		10.3

		12		12

		12.7		12.7

		15.2		15.2



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth

0

0

0.2609881296

0.2486090596

0.2625922361

0.2976470461

0.3139236445

0.3574683923

0.4117741418

0.4350820558

0.4727301893

0.495682257

0.4743342958

0.5360003825

0.5545396214

0.5451900732

0.5898299647

0.5867800881

0.6154956689

0.6223958916

0.6555983317

0.6533306061

0.6764517164

0.6804953782

0.6780558229

0.697633251

0.7261790183

0.704559802

0.753448829

0.7260320763

0.7694898941

0.7453078706

0.7935514918

0.7627016843

0.7967597048

0.7784678205

0.822425409

0.7928148974

0.8368623677

0.8059161782

0.8384664742

0.8179171041

0.8448829002

0.8289409027

0.8496952198

0.8390928399

0.878569137

0.8484634945

0.88177735

0.8571313165

0.8833814565

0.8651646496

0.8897978826

0.8726233494

0.8962143086

0.879560091

0.9010266282

0.8860214341

0.9026307347

0.8920486997

0.9074430542

0.8976786962

0.9122553738

0.9029443244

0.9138594803

0.9078750865

0.9218800128

0.9124975154

0.9266923324

0.9209107931

0.9282964389

0.9247428858

0.9299005454

0.9283496304

0.9315046519

0.9317472427

0.9331087584

0.9349505144

0.9347128649

0.9379729641

0.9363169714

0.9435238795

0.944337504

0.9460741237

0.9459416105

0.9484872947

0.9507539301

0.9549894029

0.9555662496

0.9622051628

0.9571703561

0.9652965554

0.9619826756

0.9729386746

0.9651908887

0.9769480439

0.9667949952

0.979507282

0.9812319538

0.9802864525

0.9828360603

0.984306304

0.9860442733

0.9848807795

0.9892524864

0.9891013236

0.9924606994

0.993499306

0.9940648059

0.9950034199

0.9956689124

0.9970746093

0.9972730189

0.9976338343

0.9988771254

0.998853725



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		0		0

		2		2

		3		3

		4		4

		5		5

		6		6

		7		7

		8		8

		9		9

		10		10

		11		11

		13		13

		14		14

		15		15

		16		16

		17		17

		19		19

		20		20

		21		21

		22		22

		23		23

		25		25

		28		28

		30		30

		32		32

		34		34

		35		35

		36		36

		38		38

		40		40

		42		42

		44		44

		45		45

		47		47

		50		50

		51		51

		54		54

		55		55

		57		57

		60		60

		62		62

		63		63

		64		64

		65		65

		68		68

		70		70

		73		73

		74		74

		75		75

		76		76

		80		80

		83		83

		85		85

		86		86

		89		89

		90		90

		95		95

		100		100

		102		102

		108		108

		110		110

		112		112

		113		113

		115		115

		119		119

		120		120

		125		125

		127		127

		130		130

		135		135

		137		137

		138		138

		139		139

		140		140

		149		149

		150		150

		152		152

		155		155

		160		160

		165		165

		168		168

		170		170

		171		171

		176		176

		178		178

		180		180

		187		187

		190		190

		200		200

		203		203

		205		205

		210		210

		220		220

		225		225

		229		229

		230		230

		235		235

		239		239

		240		240

		241		241

		247		247

		250		250

		254		254

		255		255

		256		256

		260		260

		267		267

		270		270

		275		275

		279		279

		290		290

		300		300

		305		305

		310		310

		312		312

		319		319

		320		320

		330		330

		335		335

		350		350

		353		353

		356		356

		359		359

		370		370

		380		380

		381		381

		400		400

		420		420

		425		425

		435		435

		450		450

		457		457

		479		479

		480		480

		483		483

		500		500

		502		502

		520		520

		528		528

		559		559

		570		570

		580		580

		585		585

		598		598

		600		600

		610		610

		635		635

		650		650

		685		685

		686		686

		710		710

		718		718

		740		740

		750		750

		762		762

		770		770

		838		838

		914		914

		920		920

		930		930

		1007		1007

		1020		1020

		1118		1118

		1197		1197

		1198		1198

		1220		1220

		1250		1250

		1252		1252

		1300		1300

		1420		1420

		1473		1473

		1500		1500

		1829		1829

		2100		2100

		2500		2500

		3000		3000

		3048		3048

		7620		7620

		9144		9144



Data

Weibull Fit

L (mm)

P(L)

Gouge Length

0

0

0.0027052833

0.0221996619

0.0058879694

0.0310666047

0.0122533418

0.039389479

0.0233927435

0.0473150093

0.032940802

0.0549268218

0.0361234882

0.062278905

0.0472628899

0.0694089711

0.0520369192

0.0763448439

0.0774984087

0.083107896

0.0870464672

0.0897150613

0.1077339274

0.1025143783

0.1093252705

0.1087275184

0.1204646722

0.1148277081

0.1220560153

0.1208220332

0.1252387015

0.1267166821

0.1379694462

0.1382281593

0.1443348186

0.1438541671

0.1459261617

0.1493990348

0.1491088479

0.1548662951

0.150700191

0.1602591627

0.1968491407

0.1708332345

0.1984404838

0.1862026256

0.2207192871

0.1961460957

0.2239019733

0.2058644094

0.2286760025

0.2153702099

0.2334500318

0.2200469719

0.2382240611

0.2246747146

0.2493634628

0.2337879537

0.2636855506

0.242718957

0.2668682368

0.2514759034

0.2716422661

0.2600662418

0.2811903246

0.2643010857

0.2827816677

0.2726541195

0.3193825589

0.2849030968

0.3448440484

0.2889140261

0.3480267346

0.3007395017

0.35598345

0.3046141911

0.3575747931

0.3122662049

0.3687141948

0.3235085687

0.371896881

0.3308520409

0.3734882241

0.3344797175

0.3782622533

0.3380786

0.3798535964

0.3416491074

0.3814449395

0.3521944003

0.4053150859

0.3590899069

0.406906429

0.3692383691

0.4084977721

0.3725706105

0.4196371738

0.3758781077

0.4339592616

0.3791611763

0.4466900064

0.3920552276

0.4482813495

0.4014836993

0.4530553787

0.407658168

0.4546467218

0.4107128239

0.4562380649

0.4197494384

0.4689688097

0.4227199858

0.473742839

0.4372704979

0.5071610439

0.45133676

0.5326225334

0.4568332757

0.5342138765

0.4728963645

0.542170592

0.4781131993

0.5437619351

0.4832634712

0.5469446213

0.4858140411

0.5501273074

0.4908668174

0.5517186505

0.5007830743

0.5660407384

0.5032235427

0.5676320815

0.5152012063

0.5851368555

0.5198898874

0.5994589433

0.5268163886

0.6010502864

0.5380845508

0.6026416295

0.5424979192

0.6042329726

0.5446849301

0.6074156588

0.5468589703

0.610598345

0.5490201467

0.6121896881

0.5679088568

0.6360598345

0.5699469915

0.6774347549

0.5739880396

0.679026098

0.5799629274

0.6838001273

0.5896958096

0.6869828135

0.5991562912

0.6885741566

0.6047060415

0.7013049013

0.6083544468

0.7028962444

0.6101634474

0.7044875875

0.6190593637

0.7076702737

0.6225494899

0.7108529599

0.6260014571

0.712444303

0.637790561

0.7140356461

0.6427074878

0.7283577339

0.6585363923

0.7426798218

0.6631228305

0.7442711649

0.6661402453

0.745862508

0.6735461368

0.7506365372

0.6877895472

0.7522278803

0.6946391352

0.763367282

0.6999934127

0.7665499682

0.7013149322

0.7681413113

0.7078223569

0.7729153405

0.7129105681

0.7792807129

0.7141666063

0.780872056

0.7154163176

0.7824633991

0.7227838802

0.7904201146

0.7263853334

0.8015595162

0.7311041188

0.8031508593

0.7322692044

0.8047422024

0.7334285158

0.8063335455

0.7380087068

0.8079248886

0.7458095461

0.8111075748

0.7490714749

0.8126989179

0.7544027834

0.814290261

0.7585752998

0.8158816041

0.7696416261

0.8254296626

0.7792066512

0.8445257798

0.7838207739

0.8461171229

0.7883267606

0.8477084659

0.7900995439

0.849299809

0.7961744234

0.8508911521

0.7970260726

0.8556651814

0.8053271123

0.8572565245

0.8093349165

0.8636218969

0.8208172905

0.8699872693

0.8230202792

0.8731699554

0.8251932443

0.8747612985

0.8273366555

0.8763526416

0.8349503347

0.8779439847

0.8415506744

0.8795353278

0.8421945116

0.8843093571

0.8538956586

0.8859007002

0.8651916894

0.8874920433

0.8678637177

0.8890833864

0.8730356624

0.8922660726

0.8803837695

0.8970401018

0.8836531018

0.8986314449

0.8933111595

0.900222788

0.8937289584

0.9018141311

0.8949717413

0.9065881604

0.9017231439

0.9081795035

0.9024859997

0.9097708466

0.9090706035

0.9113621897

0.9118415332

0.9129535328

0.9217498252

0.9145448759

0.9249719361

0.9177275621

0.9277777196

0.9193189052

0.9291382157

0.9225015913

0.9325486053

0.9288669637

0.9330574854

0.9352323361

0.9355409901

0.9368236792

0.9413289215

0.9400063654

0.9445333079

0.9415977085

0.9513073242

0.9431890516

0.9514874286

0.9447803947

0.9556042744

0.9463717377

0.9568927797

0.9479630808

0.9602359154

0.9495544239

0.9616636804

0.9591024825

0.9633057211

0.9606938256

0.9643589667

0.9622851687

0.9721217511

0.9638765118

0.9787355446

0.9654678549

0.9791820766

0.967059198

0.97990457

0.9686505411

0.9846595465

0.9702418842

0.9853382611

0.9718332272

0.9895459822

0.9734245703

0.9920133817

0.9750159134

0.9920404044

0.9766072565

0.9926114708

0.9781985996

0.9933224479

0.9797899427

0.9933672452

0.9813812858

0.9943538192

0.9829726289

0.9962097064

0.984563972

0.9968159301

0.9861553151

0.997085315

0.9877466582

0.9989883233

0.9893380013

0.9995670191

0.9909293444

0.9998723691

0.9941120306

0.9999710604

0.9957033736

0.999974848

0.9972947167

0.9999999999

0.9988860598

1



		0

		2

		3

		4

		5

		6

		7

		8

		9

		10

		11

		13

		14

		15

		16

		17

		19

		20

		21

		22

		23

		25

		28

		30

		32

		34

		35

		36

		38

		40

		42

		44

		45

		47

		50

		51

		54

		55

		57

		60

		62

		63

		64

		65

		68

		70

		73

		74

		75

		76

		80

		83

		85

		86

		89

		90

		95

		100

		102

		108

		110

		112

		113

		115

		119

		120

		125

		127

		130

		135

		137

		138

		139

		140

		149

		150

		152

		155

		160

		165

		168

		170

		171

		176

		178

		180

		187

		190

		200

		203

		205

		210

		220

		225

		229

		230

		235

		239

		240

		241

		247

		250

		254

		255

		256

		260

		267

		270

		275

		279

		290

		300

		305

		310

		312

		319

		320

		330

		335

		350

		353

		356

		359

		370

		380

		381

		400

		420

		425

		435

		450

		457

		479

		480

		483

		500

		502

		520

		528

		559

		570

		580

		585

		598

		600

		610

		635

		650

		685

		686

		710

		718

		740

		750

		762

		770

		838

		914

		920

		930

		1007

		1020

		1118

		1197

		1198

		1220

		1250

		1252

		1300

		1420

		1473

		1500

		1829

		2100

		2500

		3000

		3048

		7620

		9144



Weibull Fit

L (mm)

P(L)

Gouge Length

0.0092195903

0.0085621092

0.0081066977

0.0077578318

0.0074745917

0.0072357614

0.007028954

0.0068463216

0.0066825847

0.0065340246

0.0062722419

0.0061553996

0.0060461574

0.0059435215

0.0058466834

0.0056678449

0.0055848201

0.0055055032

0.0054295524

0.005356672

0.0052191253

0.0050303388

0.004914326

0.0048050388

0.0047016945

0.0046520438

0.0046036446

0.0045103458

0.0044213381

0.0043362283

0.0042546775

0.0042151434

0.0041383914

0.0040286166

0.0039933477

0.0038911882

0.0038582826

0.0037940812

0.0037015561

0.0036422162

0.0036132087

0.0035846261

0.0035564567

0.0034743175

0.00342143

0.0033447206

0.003319816

0.0032952309

0.0032709577

0.0031768446

0.0031092076

0.0030654315

0.0030439217

0.0029808451

0.002960288

0.0028608174

0.0027665091

0.0027301302

0.0026252729

0.0025916701

0.0025587068

0.0025424587

0.0025104177

0.0024480936

0.0024328663

0.0023587514

0.0023300138

0.0022878366

0.0022199098

0.0021935322

0.0021805076

0.0021675906

0.0021547798

0.0020440513

0.0020322336

0.0020088757

0.0019745166

0.0019189912

0.001865537

0.0018344122

0.0018140431

0.0018039704

0.0017546945

0.0017354778

0.0017165345

0.0016523093

0.0016257343

0.0015410114

0.0015166957

0.0015007546

0.0014618168

0.0013876695

0.0013523541

0.0013249008

0.0013181453

0.0012849977

0.0012592147

0.0012528683

0.0012465609

0.0012095204

0.0011915032

0.0011679843

0.0011621927

0.0011564358

0.0011337502

0.0010953267

0.0010793395

0.0010533106

0.001033026

0.000979595

0.0009338408

0.0009119105

0.0008905828

0.0008822159

0.0008536472

0.0008496548

0.0008109041

0.0007923011

0.0007393864

0.0007292993

0.0007193702

0.0007095962

0.0006750386

0.0006452845

0.0006423923

0.0005901464

0.0005402851

0.0005285744

0.0005059991

0.0004741354

0.0004600388

0.000418689

0.0004169103

0.0004116242

0.0003830384

0.0003798224

0.0003521843

0.000340619

0.0002995889

0.0002863584

0.0002748837

0.0002693354

0.000255473

0.0002534102

0.0002433644

0.0002200931

0.0002072967

0.0001804593

0.0001797499

0.0001635935

0.000158561

0.0001455594

0.0001400319

0.000133694

0.0001296397

0.0001000398

0.0000752539

0.0000735966

0.0000709196

0.0000534539

0.0000509842

0.0000358227

0.0000270704

0.0000269752

0.000024967

0.000022477

0.0000223205

0.0000188864

0.0000125007

0.0000104399

0.0000095289

0.0000032042

0.0000013413

0.0000003845

0.0000000847

0.0000000734

0

0



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035115014.xls
Chart2

		0		0

		2		2

		3		3

		4		4

		5		5

		6		6

		7		7

		8		8

		9		9

		10		10

		11		11

		13		13

		14		14

		15		15

		16		16

		17		17

		19		19

		20		20

		21		21

		22		22

		23		23

		25		25

		28		28

		30		30

		32		32

		34		34

		35		35

		36		36

		38		38

		40		40

		42		42

		44		44

		45		45

		47		47

		50		50

		51		51

		54		54

		55		55

		57		57

		60		60

		62		62

		63		63

		64		64

		65		65

		68		68

		70		70

		73		73

		74		74

		75		75

		76		76

		80		80

		83		83

		85		85

		86		86

		89		89

		90		90

		95		95

		100		100

		102		102

		108		108

		110		110

		112		112

		113		113

		115		115

		119		119

		120		120

		125		125

		127		127

		130		130

		135		135

		137		137

		138		138

		139		139

		140		140

		149		149

		150		150

		152		152

		155		155

		160		160

		165		165

		168		168

		170		170

		171		171

		176		176

		178		178

		180		180

		187		187

		190		190

		200		200

		203		203

		205		205

		210		210

		220		220

		225		225

		229		229

		230		230

		235		235

		239		239

		240		240

		241		241

		247		247

		250		250

		254		254

		255		255

		256		256

		260		260

		267		267

		270		270

		275		275

		279		279

		290		290

		300		300

		305		305

		310		310

		312		312

		319		319

		320		320

		330		330

		335		335

		350		350

		353		353

		356		356

		359		359

		370		370

		380		380

		381		381

		400		400

		420		420

		425		425

		435		435

		450		450

		457		457

		479		479

		480		480

		483		483

		500		500

		502		502

		520		520

		528		528

		559		559

		570		570

		580		580

		585		585

		598		598

		600		600

		610		610

		635		635

		650		650

		685		685

		686		686

		710		710

		718		718

		740		740

		750		750

		762		762

		770		770

		838		838

		914		914

		920		920

		930		930

		1007		1007

		1020		1020

		1118		1118

		1197		1197

		1198		1198

		1220		1220

		1250		1250

		1252		1252

		1300		1300

		1420		1420

		1473		1473

		1500		1500

		1829		1829

		2100		2100

		2500		2500

		3000		3000

		3048		3048

		7620		7620

		9144		9144



Data

Weibull Fit

L (mm)

P(L)

Gouge Length

0

0

0.0027052833

0.0221996619

0.0058879694

0.0310666047

0.0122533418

0.039389479

0.0233927435

0.0473150093

0.032940802

0.0549268218

0.0361234882

0.062278905

0.0472628899

0.0694089711

0.0520369192

0.0763448439

0.0774984087

0.083107896

0.0870464672

0.0897150613

0.1077339274

0.1025143783

0.1093252705

0.1087275184

0.1204646722

0.1148277081

0.1220560153

0.1208220332

0.1252387015

0.1267166821

0.1379694462

0.1382281593

0.1443348186

0.1438541671

0.1459261617

0.1493990348

0.1491088479

0.1548662951

0.150700191

0.1602591627

0.1968491407

0.1708332345

0.1984404838

0.1862026256

0.2207192871

0.1961460957

0.2239019733

0.2058644094

0.2286760025

0.2153702099

0.2334500318

0.2200469719

0.2382240611

0.2246747146

0.2493634628

0.2337879537

0.2636855506

0.242718957

0.2668682368

0.2514759034

0.2716422661

0.2600662418

0.2811903246

0.2643010857

0.2827816677

0.2726541195

0.3193825589

0.2849030968

0.3448440484

0.2889140261

0.3480267346

0.3007395017

0.35598345

0.3046141911

0.3575747931

0.3122662049

0.3687141948

0.3235085687

0.371896881

0.3308520409

0.3734882241

0.3344797175

0.3782622533

0.3380786

0.3798535964

0.3416491074

0.3814449395

0.3521944003

0.4053150859

0.3590899069

0.406906429

0.3692383691

0.4084977721

0.3725706105

0.4196371738

0.3758781077

0.4339592616

0.3791611763

0.4466900064

0.3920552276

0.4482813495

0.4014836993

0.4530553787

0.407658168

0.4546467218

0.4107128239

0.4562380649

0.4197494384

0.4689688097

0.4227199858

0.473742839

0.4372704979

0.5071610439

0.45133676

0.5326225334

0.4568332757

0.5342138765

0.4728963645

0.542170592

0.4781131993

0.5437619351

0.4832634712

0.5469446213

0.4858140411

0.5501273074

0.4908668174

0.5517186505

0.5007830743

0.5660407384

0.5032235427

0.5676320815

0.5152012063

0.5851368555

0.5198898874

0.5994589433

0.5268163886

0.6010502864

0.5380845508

0.6026416295

0.5424979192

0.6042329726

0.5446849301

0.6074156588

0.5468589703

0.610598345

0.5490201467

0.6121896881

0.5679088568

0.6360598345

0.5699469915

0.6774347549

0.5739880396

0.679026098

0.5799629274

0.6838001273

0.5896958096

0.6869828135

0.5991562912

0.6885741566

0.6047060415

0.7013049013

0.6083544468

0.7028962444

0.6101634474

0.7044875875

0.6190593637

0.7076702737

0.6225494899

0.7108529599

0.6260014571

0.712444303

0.637790561

0.7140356461

0.6427074878

0.7283577339

0.6585363923

0.7426798218

0.6631228305

0.7442711649

0.6661402453

0.745862508

0.6735461368

0.7506365372

0.6877895472

0.7522278803

0.6946391352

0.763367282

0.6999934127

0.7665499682

0.7013149322

0.7681413113

0.7078223569

0.7729153405

0.7129105681

0.7792807129

0.7141666063

0.780872056

0.7154163176

0.7824633991

0.7227838802

0.7904201146

0.7263853334

0.8015595162

0.7311041188

0.8031508593

0.7322692044

0.8047422024

0.7334285158

0.8063335455

0.7380087068

0.8079248886

0.7458095461

0.8111075748

0.7490714749

0.8126989179

0.7544027834

0.814290261

0.7585752998

0.8158816041

0.7696416261

0.8254296626

0.7792066512

0.8445257798

0.7838207739

0.8461171229

0.7883267606

0.8477084659

0.7900995439

0.849299809

0.7961744234

0.8508911521

0.7970260726

0.8556651814

0.8053271123

0.8572565245

0.8093349165

0.8636218969

0.8208172905

0.8699872693

0.8230202792

0.8731699554

0.8251932443

0.8747612985

0.8273366555

0.8763526416

0.8349503347

0.8779439847

0.8415506744

0.8795353278

0.8421945116

0.8843093571

0.8538956586

0.8859007002

0.8651916894

0.8874920433

0.8678637177

0.8890833864

0.8730356624

0.8922660726

0.8803837695

0.8970401018

0.8836531018

0.8986314449

0.8933111595

0.900222788

0.8937289584

0.9018141311

0.8949717413

0.9065881604

0.9017231439

0.9081795035

0.9024859997

0.9097708466

0.9090706035

0.9113621897

0.9118415332

0.9129535328

0.9217498252

0.9145448759

0.9249719361

0.9177275621

0.9277777196

0.9193189052

0.9291382157

0.9225015913

0.9325486053

0.9288669637

0.9330574854

0.9352323361

0.9355409901

0.9368236792

0.9413289215

0.9400063654

0.9445333079

0.9415977085

0.9513073242

0.9431890516

0.9514874286

0.9447803947

0.9556042744

0.9463717377

0.9568927797

0.9479630808

0.9602359154

0.9495544239

0.9616636804

0.9591024825

0.9633057211

0.9606938256

0.9643589667

0.9622851687

0.9721217511

0.9638765118

0.9787355446

0.9654678549

0.9791820766

0.967059198

0.97990457

0.9686505411

0.9846595465

0.9702418842

0.9853382611

0.9718332272

0.9895459822

0.9734245703

0.9920133817

0.9750159134

0.9920404044

0.9766072565

0.9926114708

0.9781985996

0.9933224479

0.9797899427

0.9933672452

0.9813812858

0.9943538192

0.9829726289

0.9962097064

0.984563972

0.9968159301

0.9861553151

0.997085315

0.9877466582

0.9989883233

0.9893380013

0.9995670191

0.9909293444

0.9998723691

0.9941120306

0.9999710604

0.9957033736

0.999974848

0.9972947167

0.9999999999

0.9988860598

1



gouge depth

		

		depth		P(a)		fit		p(a) fit

		0		0		0

		0.1		0.2609881296		0.2486090596		1.3530476833

		0.14		0.2625922361		0.2976470461		1.116696584

		0.2		0.3139236445		0.3574683923		0.8952834282

		0.3		0.4117741418		0.4350820558		0.6774818322

		0.4		0.4727301893		0.495682257		0.5437373905

		0.48		0.4743342958		0.5360003825		0.4676333891

		0.5		0.5545396214		0.5451900732		0.4515004433

		0.6		0.5898299647		0.5867800881		0.3834532524

		0.7		0.6154956689		0.6223958916		0.3309768236

		0.8		0.6555983317		0.6533306061		0.2892140277

		0.9		0.6764517164		0.6804953782		0.25518466

		0.97		0.6780558229		0.697633251		0.2348960081

		1		0.7261790183		0.704559802		0.2269429696

		1.1		0.753448829		0.7260320763		0.2031568977

		1.2		0.7694898941		0.7453078706		0.1828797464

		1.3		0.7935514918		0.7627016843		0.1654179989

		1.4		0.7967597048		0.7784678205		0.1502507313

		1.5		0.822425409		0.7928148974		0.1369783424

		1.6		0.8368623677		0.8059161782		0.1252887538

		1.7		0.8384664742		0.8179171041		0.1149344438

		1.8		0.8448829002		0.8289409027		0.1057164319

		1.9		0.8496952198		0.8390928399		0.0974728546

		2		0.878569137		0.8484634945		0.0900706542

		2.1		0.88177735		0.8571313165		0.083399424

		2.2		0.8833814565		0.8651646496		0.0773667803

		2.3		0.8897978826		0.8726233494		0.071894832

		2.4		0.8962143086		0.879560091		0.0669174537

		2.5		0.9010266282		0.8860214341		0.0623781561

		2.6		0.9026307347		0.8920486997		0.058228404

		2.7		0.9074430542		0.8976786962		0.0544262761

		2.8		0.9122553738		0.9029443244		0.0509353873

		2.9		0.9138594803		0.9078750865		0.0477240158

		3		0.9218800128		0.9124975154		0.0447643897

		3.2		0.9266923324		0.9209107931		0.0395056195

		3.3		0.9282964389		0.9247428858		0.0371658911

		3.4		0.9299005454		0.9283496304		0.034995998

		3.5		0.9315046519		0.9317472427		0.0329808749

		3.6		0.9331087584		0.9349505144		0.0311070687

		3.7		0.9347128649		0.9379729641		0.0293625343

		3.9		0.9363169714		0.9435238795		0.0262191193

		4		0.944337504		0.9460741237		0.0248017406

		4.1		0.9459416105		0.9484872947		0.0234763988

		4.4		0.9507539301		0.9549894029		0.0199840925

		4.8		0.9555662496		0.9622051628		0.0162487654

		5		0.9571703561		0.9652965554		0.0146960571

		5.6		0.9619826756		0.9729386746		0.0109892142

		6		0.9651908887		0.9769480439		0.0091251281

		6.3		0.9667949952		0.979507282		0.0079669246

		6.4		0.9812319538		0.9802864525		0.0076194801

		7		0.9828360603		0.984306304		0.005867946

		7.1		0.9860442733		0.9848807795		0.0056235552

		8		0.9892524864		0.9891013236		0.0038786234

		9.5		0.9924606994		0.993499306		0.0021709466

		10.3		0.9940648059		0.9950034199		0.00161946

		12		0.9956689124		0.9970746093		0.0008960536

		12.7		0.9972730189		0.9976338343		0.0007097165

		15.2		0.9988771254		0.998853725		0.0003217021





gouge depth

		



Data

Weibull Fit

a (mm)

P(a)

Gouge Depth



gouge length

		



Weibull Fit

a (mm)

P(a)

Gouge Depth



force

		

		L		P(L)		fit		p(a) fit

		0		0		0

		2		0.0027052833		0.0221996619		0.0092195903

		3		0.0058879694		0.0310666047		0.0085621092

		4		0.0122533418		0.039389479		0.0081066977

		5		0.0233927435		0.0473150093		0.0077578318

		6		0.032940802		0.0549268218		0.0074745917

		7		0.0361234882		0.062278905		0.0072357614

		8		0.0472628899		0.0694089711		0.007028954

		9		0.0520369192		0.0763448439		0.0068463216

		10		0.0774984087		0.083107896		0.0066825847

		11		0.0870464672		0.0897150613		0.0065340246

		13		0.1077339274		0.1025143783		0.0062722419

		14		0.1093252705		0.1087275184		0.0061553996

		15		0.1204646722		0.1148277081		0.0060461574

		16		0.1220560153		0.1208220332		0.0059435215

		17		0.1252387015		0.1267166821		0.0058466834

		19		0.1379694462		0.1382281593		0.0056678449

		20		0.1443348186		0.1438541671		0.0055848201

		21		0.1459261617		0.1493990348		0.0055055032

		22		0.1491088479		0.1548662951		0.0054295524

		23		0.150700191		0.1602591627		0.005356672

		25		0.1968491407		0.1708332345		0.0052191253

		28		0.1984404838		0.1862026256		0.0050303388

		30		0.2207192871		0.1961460957		0.004914326

		32		0.2239019733		0.2058644094		0.0048050388

		34		0.2286760025		0.2153702099		0.0047016945

		35		0.2334500318		0.2200469719		0.0046520438

		36		0.2382240611		0.2246747146		0.0046036446

		38		0.2493634628		0.2337879537		0.0045103458

		40		0.2636855506		0.242718957		0.0044213381

		42		0.2668682368		0.2514759034		0.0043362283

		44		0.2716422661		0.2600662418		0.0042546775

		45		0.2811903246		0.2643010857		0.0042151434

		47		0.2827816677		0.2726541195		0.0041383914

		50		0.3193825589		0.2849030968		0.0040286166

		51		0.3448440484		0.2889140261		0.0039933477

		54		0.3480267346		0.3007395017		0.0038911882

		55		0.35598345		0.3046141911		0.0038582826

		57		0.3575747931		0.3122662049		0.0037940812

		60		0.3687141948		0.3235085687		0.0037015561

		62		0.371896881		0.3308520409		0.0036422162

		63		0.3734882241		0.3344797175		0.0036132087

		64		0.3782622533		0.3380786		0.0035846261

		65		0.3798535964		0.3416491074		0.0035564567

		68		0.3814449395		0.3521944003		0.0034743175

		70		0.4053150859		0.3590899069		0.00342143

		73		0.406906429		0.3692383691		0.0033447206

		74		0.4084977721		0.3725706105		0.003319816

		75		0.4196371738		0.3758781077		0.0032952309

		76		0.4339592616		0.3791611763		0.0032709577

		80		0.4466900064		0.3920552276		0.0031768446

		83		0.4482813495		0.4014836993		0.0031092076

		85		0.4530553787		0.407658168		0.0030654315

		86		0.4546467218		0.4107128239		0.0030439217

		89		0.4562380649		0.4197494384		0.0029808451

		90		0.4689688097		0.4227199858		0.002960288

		95		0.473742839		0.4372704979		0.0028608174

		100		0.5071610439		0.45133676		0.0027665091

		102		0.5326225334		0.4568332757		0.0027301302

		108		0.5342138765		0.4728963645		0.0026252729

		110		0.542170592		0.4781131993		0.0025916701

		112		0.5437619351		0.4832634712		0.0025587068

		113		0.5469446213		0.4858140411		0.0025424587

		115		0.5501273074		0.4908668174		0.0025104177

		119		0.5517186505		0.5007830743		0.0024480936

		120		0.5660407384		0.5032235427		0.0024328663

		125		0.5676320815		0.5152012063		0.0023587514

		127		0.5851368555		0.5198898874		0.0023300138

		130		0.5994589433		0.5268163886		0.0022878366

		135		0.6010502864		0.5380845508		0.0022199098

		137		0.6026416295		0.5424979192		0.0021935322

		138		0.6042329726		0.5446849301		0.0021805076

		139		0.6074156588		0.5468589703		0.0021675906

		140		0.610598345		0.5490201467		0.0021547798

		149		0.6121896881		0.5679088568		0.0020440513

		150		0.6360598345		0.5699469915		0.0020322336

		152		0.6774347549		0.5739880396		0.0020088757

		155		0.679026098		0.5799629274		0.0019745166

		160		0.6838001273		0.5896958096		0.0019189912

		165		0.6869828135		0.5991562912		0.001865537

		168		0.6885741566		0.6047060415		0.0018344122

		170		0.7013049013		0.6083544468		0.0018140431

		171		0.7028962444		0.6101634474		0.0018039704

		176		0.7044875875		0.6190593637		0.0017546945

		178		0.7076702737		0.6225494899		0.0017354778

		180		0.7108529599		0.6260014571		0.0017165345

		187		0.712444303		0.637790561		0.0016523093

		190		0.7140356461		0.6427074878		0.0016257343

		200		0.7283577339		0.6585363923		0.0015410114

		203		0.7426798218		0.6631228305		0.0015166957

		205		0.7442711649		0.6661402453		0.0015007546

		210		0.745862508		0.6735461368		0.0014618168

		220		0.7506365372		0.6877895472		0.0013876695

		225		0.7522278803		0.6946391352		0.0013523541

		229		0.763367282		0.6999934127		0.0013249008

		230		0.7665499682		0.7013149322		0.0013181453

		235		0.7681413113		0.7078223569		0.0012849977

		239		0.7729153405		0.7129105681		0.0012592147

		240		0.7792807129		0.7141666063		0.0012528683

		241		0.780872056		0.7154163176		0.0012465609

		247		0.7824633991		0.7227838802		0.0012095204

		250		0.7904201146		0.7263853334		0.0011915032

		254		0.8015595162		0.7311041188		0.0011679843

		255		0.8031508593		0.7322692044		0.0011621927

		256		0.8047422024		0.7334285158		0.0011564358

		260		0.8063335455		0.7380087068		0.0011337502

		267		0.8079248886		0.7458095461		0.0010953267

		270		0.8111075748		0.7490714749		0.0010793395

		275		0.8126989179		0.7544027834		0.0010533106

		279		0.814290261		0.7585752998		0.001033026

		290		0.8158816041		0.7696416261		0.000979595

		300		0.8254296626		0.7792066512		0.0009338408

		305		0.8445257798		0.7838207739		0.0009119105

		310		0.8461171229		0.7883267606		0.0008905828

		312		0.8477084659		0.7900995439		0.0008822159

		319		0.849299809		0.7961744234		0.0008536472

		320		0.8508911521		0.7970260726		0.0008496548

		330		0.8556651814		0.8053271123		0.0008109041

		335		0.8572565245		0.8093349165		0.0007923011

		350		0.8636218969		0.8208172905		0.0007393864

		353		0.8699872693		0.8230202792		0.0007292993

		356		0.8731699554		0.8251932443		0.0007193702

		359		0.8747612985		0.8273366555		0.0007095962

		370		0.8763526416		0.8349503347		0.0006750386

		380		0.8779439847		0.8415506744		0.0006452845

		381		0.8795353278		0.8421945116		0.0006423923

		400		0.8843093571		0.8538956586		0.0005901464

		420		0.8859007002		0.8651916894		0.0005402851

		425		0.8874920433		0.8678637177		0.0005285744

		435		0.8890833864		0.8730356624		0.0005059991

		450		0.8922660726		0.8803837695		0.0004741354

		457		0.8970401018		0.8836531018		0.0004600388

		479		0.8986314449		0.8933111595		0.000418689

		480		0.900222788		0.8937289584		0.0004169103

		483		0.9018141311		0.8949717413		0.0004116242

		500		0.9065881604		0.9017231439		0.0003830384

		502		0.9081795035		0.9024859997		0.0003798224

		520		0.9097708466		0.9090706035		0.0003521843

		528		0.9113621897		0.9118415332		0.000340619

		559		0.9129535328		0.9217498252		0.0002995889

		570		0.9145448759		0.9249719361		0.0002863584

		580		0.9177275621		0.9277777196		0.0002748837

		585		0.9193189052		0.9291382157		0.0002693354

		598		0.9225015913		0.9325486053		0.000255473

		600		0.9288669637		0.9330574854		0.0002534102

		610		0.9352323361		0.9355409901		0.0002433644

		635		0.9368236792		0.9413289215		0.0002200931

		650		0.9400063654		0.9445333079		0.0002072967

		685		0.9415977085		0.9513073242		0.0001804593

		686		0.9431890516		0.9514874286		0.0001797499

		710		0.9447803947		0.9556042744		0.0001635935

		718		0.9463717377		0.9568927797		0.000158561

		740		0.9479630808		0.9602359154		0.0001455594

		750		0.9495544239		0.9616636804		0.0001400319

		762		0.9591024825		0.9633057211		0.000133694

		770		0.9606938256		0.9643589667		0.0001296397

		838		0.9622851687		0.9721217511		0.0001000398

		914		0.9638765118		0.9787355446		0.0000752539

		920		0.9654678549		0.9791820766		0.0000735966

		930		0.967059198		0.97990457		0.0000709196

		1007		0.9686505411		0.9846595465		0.0000534539

		1020		0.9702418842		0.9853382611		0.0000509842

		1118		0.9718332272		0.9895459822		0.0000358227

		1197		0.9734245703		0.9920133817		0.0000270704

		1198		0.9750159134		0.9920404044		0.0000269752

		1220		0.9766072565		0.9926114708		0.000024967

		1250		0.9781985996		0.9933224479		0.000022477

		1252		0.9797899427		0.9933672452		0.0000223205

		1300		0.9813812858		0.9943538192		0.0000188864

		1420		0.9829726289		0.9962097064		0.0000125007

		1473		0.984563972		0.9968159301		0.0000104399

		1500		0.9861553151		0.997085315		0.0000095289

		1829		0.9877466582		0.9989883233		0.0000032042

		2100		0.9893380013		0.9995670191		0.0000013413

		2500		0.9909293444		0.9998723691		0.0000003845

		3000		0.9941120306		0.9999710604		0.0000000847

		3048		0.9957033736		0.999974848		0.0000000734

		7620		0.9972947167		0.9999999999		0

		9144		0.9988860598		1		0





force

		



Data

Weibull Fit

L (mm)

P(L)

Gouge Length



		



Weibull Fit

L (mm)

P(L)

Gouge Length



		

		F		P(F)		fit		p(F) fit

		0		0		0		0

		33		0.0126353791		0.0746593717		0.0046126247

		39		0.0306859206		0.1046751313		0.0053812589

		40		0.0667870036		0.1101171321		0.0055023843

		41		0.0848375451		0.1156791714		0.0056213245

		42		0.1028880866		0.1213590305		0.0057380131

		43		0.1209386282		0.1271544257		0.005852386

		47		0.1570397112		0.1514435356		0.0062855202

		49		0.1750902527		0.164217522		0.0064866991

		52		0.2111913357		0.1841059778		0.0067681251

		57		0.2292418773		0.2190071828		0.0071802201

		61		0.2472924188		0.24829652		0.0074563598

		64		0.2833935018		0.2709349703		0.0076313034

		66		0.3014440433		0.2863007675		0.0077324179

		67		0.3375451264		0.2940563863		0.0077782997

		68		0.3916967509		0.3018563267		0.0078210609

		73		0.4097472924		0.3414117363		0.0079881548

		74		0.4277978339		0.3494122118		0.0080122836

		75		0.463898917		0.3574352807		0.0080333441

		77		0.5180505415		0.3735369758		0.0080663291

		81		0.536101083		0.4058781492		0.0080963566

		86		0.5541516245		0.4463204086		0.008068776

		90		0.5722021661		0.4784667452		0.0079973204

		96		0.5902527076		0.5259448571		0.007814182

		97		0.6083032491		0.5337398423		0.0077754141

		98		0.6624548736		0.541494946		0.0077344282

		102		0.6805054152		0.5720735457		0.007549396

		103		0.6985559567		0.579597476		0.0074981459

		111		0.7346570397		0.6377616231		0.0070253356

		112		0.7527075812		0.6447540446		0.0069592784

		116		0.7707581227		0.6720435438		0.0066822084

		117		0.7888086643		0.6786897538		0.0066100329

		120		0.8068592058		0.6981881807		0.0063874883

		122		0.8249097473		0.7108109097		0.0062347034

		128		0.8429602888		0.7468060793		0.0057602233

		130		0.8610108303		0.7581647241		0.0055981829

		137		0.8790613718		0.7953463497		0.00502409

		149		0.8971119134		0.8497608184		0.0040519372

		175		0.9151624549		0.930451232		0.0022459648

		190		0.9332129964		0.9581413687		0.0014821765

		253		0.9512635379		0.9970430189		0.000144296

		339		0.9693140794		0.9999801885		0.0000013417

		393		0.9873646209		0.9999996318		0.0000000294





		



Data

Weibull Fit

F (kN)

P(F)

Denting Force



		



Weibull Fit

F (kN)

P(F)

Denting Force




_1035112862.unknown

